## Combined Works to Go
Date Added | Room ID | Tower A or B | Room Name | Item No per room | Idenitifed by | Outstanding Work listed | Sequence | BUJV Status | QIC status onsite inspection | Required completion date | Owner of action | General notes other comments
2026-10-15 | PB01M01 | A | Entrance Facility Room | 1 | QIC | Cut/remove door strap or frame obstruction from Door Frame No. 2 | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 2 | QIC | Complete pulling of all cables into all cast-in electrical boxes | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 3 | QIC | Complete plastering to all wall chasers | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 4 | QIC | Complete all cable tray droppers to cabinets | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 5 | QIC | Cut and seal all containment at floor level | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 6 | QIC | Complete all outstanding cable pulling within containment at ceiling level | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 7 | QIC | Minimise oversized wall penetrations and seal completed cable tray penetrations after cable pulling | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 8 | QIC | Extend cable tray down to the electrical DB board; pull and cut cables to length; terminate at the DB board | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 9 | QIC | Remove all rubbish, clean the floor and maintain the room in a clean condition | 09 - Final clean / handover | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 10 | QIC | Remove surplus wall fixings that are no longer required | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 11 | QIC | Complete high-level cable terminations and install box covers | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 12 | QIC | Cut off all surplus threaded rod attached to cable trays | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 13 | QIC | Complete installation of all third-fix electrical elements, including lights, sockets, power points and switches | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 14 | QIC | Complete wall painting | 06 - Finishes / painting | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 15 | QIC | Cover and seal all unused boxes or points at floor and wall level | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M01 | A | Entrance Facility Room | 16 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M01 | A | Entrance Facility Room | 17 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M01 | A | Entrance Facility Room | 18 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M01 | A | Entrance Facility Room | 19 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M02 | A | Main Telephone Room | 1 | QIC | Cut/remove door strap or frame obstruction from Door Frame No. 2 | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 2 | QIC | Complete pulling of all cables into all cast-in electrical boxes | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 3 | QIC | Complete plastering to all wall chasers | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 4 | QIC | Complete all cable tray droppers to cabinets | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 5 | QIC | Cut and seal all containment at floor level | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 6 | QIC | Complete all outstanding cable pulling within containment at ceiling level | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 7 | QIC | Minimise oversized wall penetrations and seal completed cable tray penetrations after cable pulling | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 8 | QIC | Extend cable tray down to the electrical DB board; pull and cut cables to length; terminate at the DB board | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 9 | QIC | Remove all rubbish, clean the floor and maintain the room in a clean condition | 09 - Final clean / handover | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 10 | QIC | Remove surplus wall fixings that are no longer required | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 11 | QIC | Complete high-level cable terminations and install box covers | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 12 | QIC | Cut off all surplus threaded rod attached to cable trays | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 13 | QIC | Complete installation of all third-fix electrical elements, including lights, sockets, power points and switches | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 14 | QIC | Complete wall painting | 06 - Finishes / painting | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 15 | QIC | Cover and seal all unused boxes or points at floor and wall level | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M02 | A | Main Telephone Room | 16 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M02 | A | Main Telephone Room | 17 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M02 | A | Main Telephone Room | 18 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M02 | A | Main Telephone Room | 19 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M03 | A | GSM Room | 1 | QIC | Complete all outstanding cable tray installation within the room | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 2 | QIC | Complete pulling of cables through all conduits and into conduit boxes | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 3 | QIC | Install cover plates to all completed electrical boxes | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 4 | QIC | Complete installation of all light fittings | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 5 | QIC | Complete installation of the fire alarm system at ceiling level | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 6 | QIC | Close and make good the ceiling around all openings and service penetrations | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 7 | QIC | Minimise and seal all completed wall penetrations | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 8 | QIC | Render and make good the blockwork above the door, coordinating access around the installed ductwork | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 9 | QIC | Complete the door-frame strapping and associated door-frame fixing works | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 10 | QIC | Position and secure all cabinets within the room | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 11 | QIC | Install all droppers from the cable trays to the cabinets, ready for cable pulling | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 12 | QIC | Pull all required cables into the room and cabinets after completion of the droppers | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 13 | QIC | Complete and terminate all earthing cables | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 14 | QIC | Complete wall painting throughout the room | 06 - Finishes / painting | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 15 | QIC | Remove masking tape at floor level and rectify the affected finished-floor edges | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 16 | QIC | Seal and make good the gap between the door frame and the adjacent wall | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 17 | QIC | Inspect and rectify the wall nib on the hinge side so that it is square and aligned with the main wall | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 18 | QIC | Complete all third-fix electrical works, including light switches, wall sockets, power points and associated accessories | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 19 | QIC | Remove all rubbish and complete a general clean of the room | 09 - Final clean / handover | Outstanding
2026-10-15 | PB01M03 | A | GSM Room | 20 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M03 | A | GSM Room | 21 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M03 | A | GSM Room | 22 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Tetra Room | A | Tetra Room | 1 | QIC | Complete final plastering around the door frame | 04 - Wet works / builder works | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 2 | QIC | Complete third-fix installation of all light switches and power points on the walls | 07 - Final fix / terminations | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 3 | QIC | Complete pulling of all cables into the room | 03 - MEP first / second fix | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 4 | QIC | Install cover plates to all MEP boxes | 07 - Final fix / terminations | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 5 | QIC | Complete the cable tray installation | 03 - MEP first / second fix | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 6 | QIC | Pull all required cables and install droppers into the room where required | 03 - MEP first / second fix | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 7 | QIC | Install all light fittings | 07 - Final fix / terminations | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 8 | QIC | Complete earthing works inside the room | 03 - MEP first / second fix | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 9 | QIC | Complete final painting | 06 - Finishes / painting | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 10 | QIC | Seal and cover all unused openings in the floor | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 11 | QIC | Patch and seal all unused openings and penetrations in the ceiling | 04 - Wet works / builder works | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 12 | QIC | Cut off and make safe any unused or excessively extended threaded rods | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 13 | QIC | Plaster and paint the sealed wall penetration above the door on the right-hand side | 04 - Wet works / builder works | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 14 | QIC | Remove masking tape between the floor epoxy and wall paint | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 15 | QIC | Remove unused brackets from the rear wall at the end of the room | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 16 | QIC | Complete sealant at the wall-to-floor joint in the right-hand corner upon entering the room | 04 - Wet works / builder works | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 17 | QIC | Complete plaster repairs and repaint the high-level wall area on the right-hand side upon entering the room | 04 - Wet works / builder works | Outstanding
2026-10-15 | Tetra Room | A | Tetra Room | 18 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Tetra Room | A | Tetra Room | 19 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Tetra Room | A | Tetra Room | 20 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 1 | QIC | Install the external door frame, door leaf and all associated door hardware | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 2 | QIC | Following installation of the external door, complete plastering and sealant around the door frame | 04 - Wet works / builder works | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 3 | QIC | Install the required threshold and complete epoxy floor patching and rectification around the external door frame | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 4 | QIC | Patch, plaster and touch up wall finishes around all corridor door openings | 04 - Wet works / builder works | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 5 | QIC | Complete plastering and final finishes around the five internal door openings | 04 - Wet works / builder works | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 6 | QIC | Install outstanding door hardware to the internal doors | 07 - Final fix / terminations | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 7 | QIC | Investigate and rectify peeling epoxy to the wall skirting, including checking substrate preparation; raise an NCR if required | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 8 | QIC | Install the outstanding SNC wall panel | 07 - Final fix / completion | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 9 | QIC | Seal the wall penetration above the external door | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 10 | QIC | Seal penetrations above the external door associated with sprinkler lines | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 11 | QIC | Complete final painting to welded sprinkler pipework | 03 - MEP first / second fix | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 12 | QIC | Confirm whether the large ceiling opening, approximately 2 m long by 600 mm wide, is permanent; close and make good if not required | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 13 | QIC | Pull all cables through the high-level conduits | 03 - MEP first / second fix | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 14 | QIC | Terminate all cables | 07 - Final fix / terminations | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 15 | QIC | Install cover plates to all electrical and MEP boxes | 07 - Final fix / terminations | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 16 | QIC | Install all light fittings | 07 - Final fix / terminations | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 17 | QIC | Install all smoke detectors | 07 - Final fix / terminations | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 18 | QIC | Complete sealant around all openings | 07 - Final fix / completion | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 19 | QIC | Complete plastering and making good around penetrations | 04 - Wet works / builder works | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 20 | QIC | Seal all outstanding penetrations | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 21 | QIC | Remove all unused high-level fixings and patch the affected surfaces | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 22 | QIC | Touch up and make good the boards and adjacent finishes as required | 06 - Finishes / painting | Outstanding
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 23 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 24 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Back of House Circulation Corridor | A | Back of House Circulation Corridor | 25 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Generator Room | A | Generator Room | 1 | QIC | Supply and install louvre No. 1 | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 2 | QIC | Supply and install louvre No. 2 | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 3 | QIC | Supply and install louvre No. 3 | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 4 | QIC | Complete plastering and making good around all three louvres after installation | 04 - Wet works / builder works | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 5 | QIC | Supply and install the generator room double-door set, including frames and door hardware | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 6 | QIC | Grout the installed double-door frames and complete plastering and making good around the doors | 04 - Wet works / builder works | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 7 | QIC | Remove stored doors and door frames from the generator room and install them in their correct locations | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 8 | QIC | Complete cable pulling to all high-level cable trays and dress the cables properly | 03 - MEP first / second fix | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 9 | QIC | Terminate all surplus cable currently rolled up in the room and remove any redundant cable | 07 - Final fix / terminations | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 10 | QIC | Complete cable pulling to all wall-mounted floor boxes and containment | 03 - MEP first / second fix | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 11 | QIC | Complete terminations and install cover plates to wall-mounted boxes and containment | 03 - MEP first / second fix | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 12 | QIC | Seal all external penetrations leading through the generator room external walls, including around the generator exhaust area | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 13 | QIC | Following completion of all works, patch, make good and repaint all walls | 06 - Finishes / painting | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 14 | QIC | Repair and reinstate defective epoxy finishes where required | 04 - Wet works / builder works | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 15 | QIC | Review and rectify the multiple cracks in the floor near the floor drain beside the generator | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 16 | QIC | Complete termination of all earthing cables | 03 - MEP first / second fix | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 17 | QIC | Install missing sprinkler heads and confirm whether the sprinkler system installation and pressure testing have been completed | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 18 | QIC | Inspect the generator for incomplete works once the protective covering is removed | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 19 | QIC | Install missing bolts and correctly torque all generator exhaust pipework flange bolts, including at high level within the ceiling zone | 03 - MEP first / second fix | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 20 | QIC | Install cover plates to all outstanding high-level boxes | 07 - Final fix / terminations | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 21 | QIC | Remove or cut back excessively extended threaded rods and make good | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 22 | QIC | Install all light fittings throughout the room | 07 - Final fix / terminations | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 23 | QIC | Install all smoke detectors | 07 - Final fix / terminations | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 24 | QIC | Remove the sprinkler installation machine, tools and stored materials from the room; the room is no longer to be used as a work or storage area | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 25 | QIC | Complete all outstanding third-fix works and terminations | 07 - Final fix / terminations | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 26 | QIC | Confirm whether the generator exhaust requires insulation and install insulation if required | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 27 | QIC | Repair or replace the damaged kerb beneath the generator fuel tank | 04 - Wet works / builder works | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 28 | QIC | Remove all rubbish and food waste from around and beneath the generator and clean the area | 09 - Final clean / handover | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 29 | QIC | Confirm that the area beneath the fuel tank is correctly tanked and suitable to contain any fuel leakage | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 30 | QIC | Seal and make fit for purpose the large floor opening behind the fuel tank and kerb | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 31 | QIC | Seal and make fit for purpose the large wall opening behind the fuel tank and kerb | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 32 | QIC | Review floor penetrations behind the fuel tank; use and complete required conduits, or cut off and seal redundant conduits and penetrations | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 33 | QIC | Fill, screed and reinstate the floor patch near the main generator room entrance door | 04 - Wet works / builder works | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 34 | QIC | Review wall penetrations; pull cables through required penetrations, and cut, cap and seal all redundant penetrations | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 35 | QIC | Fill and make good all unused ceiling penetrations | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 36 | QIC | Remove all redundant ceiling fixtures and fixings, cut back as required, and patch and make good | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 37 | QIC | Complete and make good all MEP services to the ceiling and walls | 03 - MEP first / second fix | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 38 | QIC | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-15 | Generator Room | A | Generator Room | 39 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Generator Room | A | Generator Room | 40 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Generator Room | A | Generator Room | 41 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M06 | A | MV Room | 1 | QIC | Supply and install the missing main entrance door, door frame and associated door hardware | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 2 | QIC | Following installation of permanent conditioned air, review and remove the two temporary split air-conditioning systems | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 3 | QIC | Seal the penetrations above the entrance door now that cable pulling is complete | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 4 | QIC | Complete all high-level cable terminations and install cover plates to all conduit boxes | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 5 | QIC | Install the outstanding air-conditioning supply and/or return air grilles | 07 - Final fix / completion | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 6 | QIC | Complete third-fix installation to all wall boxes, switches and power points | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 7 | QIC | Modify the floor cover/grate to accommodate the containment to the right-hand side of the entrance door, then install the grate correctly | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 8 | QIC | Maintain the room in a clean condition at all times due to the installed equipment | 09 - Final clean / handover | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 9 | QIC | Repaint the expansion joints to the left-hand side of the entrance door | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 10 | QIC | Seal all unused floor penetrations adjacent to the earthing system | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 11 | QIC | Complete cable termination to all wall-mounted light fittings | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 12 | QIC | Complete final termination of the fire and life-safety system cabling and install all required cover plates | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 13 | QIC | Install the outstanding sprinkler heads/nozzles and complete the sprinkler system final fix | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 14 | QIC | Review the two loose floor cover plates and either install them in their correct locations or remove them if surplus | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 15 | QIC | Confirm the purpose and status of the unconnected fourth fire-system tank, including whether it is a spare or requires connection | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 16 | QIC | Inspect the underfloor area and confirm that access is clear and the area is clean and free of outstanding works | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 17 | QIC | Complete all remaining third-fix works to every component in the room | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 18 | QIC | Carry out final cleaning and prepare the room for snagging and secure close-out | 08 - Testing / commissioning / snagging | Outstanding
2026-10-15 | PB01M06 | A | MV Room | 19 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M06 | A | MV Room | 20 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M06 | A | MV Room | 21 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 1 | QIC | Grout the installed door frame, then complete plastering and making good around the frame and adjacent wall | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 2 | QIC | Remove the two double-door frames and doors stored in the Generator Room and install them in Transformer Room - 01 as soon as possible | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 3 | QIC | Adjust and cut all floor plates to size so they are level and flush with the finished floor | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 4 | QIC | Complete termination of all earthing cables | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 5 | QIC | Complete installation of the remaining louvres on the right-hand side of the room; approximately 70% are currently installed | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 6 | QIC | Complete plastering and finishing around all installed louvres | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 7 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 8 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 9 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 10 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 11 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 12 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M37 | A | Transformer Room - 01 | 13 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 1 | QIC | Install the outstanding door and door frame | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 2 | QIC | Complete plastering, sealing and making good around the installed door frame | 04 - Wet works / builder works | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 3 | QIC | Install, adjust and make good all floor grates / cover plates so they are level and flush | 04 - Wet works / builder works | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 4 | QIC | Complete cable pulling through all high-level containment | 03 - MEP first / second fix | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 5 | QIC | Complete termination of all high-level cables | 07 - Final fix / terminations | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 6 | QIC | Install cover plates to all high-level MEP / electrical boxes | 07 - Final fix / terminations | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 7 | QIC | Install all outstanding light fixtures | 07 - Final fix / completion | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 8 | QIC | Install all outstanding smoke detectors | 07 - Final fix / terminations | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 9 | QIC | Complete third-fix works to all wall boxes, light switches and power points | 07 - Final fix / terminations | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 10 | QIC | Install any remaining wall-mounted panels | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 11 | QIC | Install DDC-03 panel by SNC | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 12 | QIC | Extend containment down to the DDC-03 panel to allow final connections | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 13 | QIC | Complete final wall painting after panel and containment works are finished | 03 - MEP first / second fix | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 14 | QIC | Seal and patch all miscellaneous or surplus wall penetrations | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 15 | QIC | Seal and patch all miscellaneous or surplus ceiling penetrations | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 16 | QIC | Clean and remove plaster and paint contamination from containment | 03 - MEP first / second fix | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 17 | QIC | Inspect trenching beneath floor cover plates and clean / clear as required | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 18 | QIC | Complete all sealant around AC openings in the ceiling | 03 - MEP first / second fix | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 19 | QIC | Replace damaged threaded rod supporting cable trays | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 20 | QIC | Cut and remove surplus threaded rod below cable trays | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 21 | QIC | Complete all remaining ceiling works and final making good | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 22 | QIC | Complete all remaining MEP second-fix and third-fix works within the room | 03 - MEP first / second fix | Outstanding
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 23 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 24 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 25 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Transformer Room - 02 | A | Transformer Room - 02 | 26 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 1 | QIC | Complete electrical termination of the roller shutter door and test and commission the shutter. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 2 | QIC | Complete missing tiling at the base of the roller shutter door and within the door track. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 3 | QIC | Complete wall tiling around MEP services. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 4 | QIC | MEP team to confirm whether wall-mounted boxes and pipes are still required so wall tiling can be completed. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 5 | QIC | Cut floor-waste pipework to the correct level, install floor grates and complete surrounding tiling. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 6 | QIC | Complete wall routing / chases and make good. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 7 | QIC | Complete third-fix electrical works. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 8 | QIC | Install and complete outstanding door frames. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 9 | QIC | Complete plastering and making good around door frames. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 10 | QIC | Complete remaining tiling works. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 11 | QIC | Complete expansion joints in wall tiling. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 12 | QIC | Complete expansion joints in floor tiling. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 13 | QIC | Complete high-level MEP third-fix works. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 14 | QIC | Install all outstanding light fittings, light boxes and power points. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 15 | QIC | Patch and paint around all high-level MEP fixings. | 06 - Finishes / painting | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 16 | QIC | Clean and complete painting to high-level fire mains. | 06 - Finishes / painting | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 17 | QIC | Complete high-level plastering, making good and painting. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 18 | QIC | Complete floor sealant and floor expansion joints. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 19 | QIC | Repair the concrete patch above the double doors leading into the corridor. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 20 | QIC | Complete insulation to all outstanding pipework. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 21 | QIC | Remove all temporary protection from MEP equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 22 | QIC | Complete all outstanding mechanical ductwork. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 23 | QIC | Complete all cable tray installation. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 24 | QIC | Dress all cables within cable trays. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 25 | QIC | Cut off and remove surplus or unused threaded rod. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 26 | QIC | Confirm all wall penetrations are required and complete fire sealant to all completed openings through walls. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 27 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 28 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Review / Refuge Room | A | Review Room / Refuge Room | 29 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M10 | A | LV Room | 1 | QIC | Verify the installed door-frame height against the approximately 150 mm raised room floor level and confirm the door opening is acceptable before proceeding. | 01 - Verify / inspect / confirm | Outstanding |  |  |  | Door frame is set to corridor level; room floor is approximately 150 mm higher.
2026-10-15 | PB01M10 | A | LV Room | 2 | QIC | Once door-frame height is verified, grout the door frames and complete plastering and making good around them. | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 3 | QIC | Complete all outstanding third-fix wall electrical items, including power points, light switches and fire-alarm switches. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 4 | QIC | Complete pulling and dressing of all high-level cables in cable trays and conduits. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 5 | QIC | Complete high-level cable terminations and install cover plates to all boxes. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 6 | QIC | Complete termination of all cables to panels. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 7 | QIC | Address and terminate all earthing cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 8 | QIC | Cut back and seal all redundant or excess floor-level penetrations. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 9 | QIC | Complete all remaining high-level third-fix works and cable terminations. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 10 | QIC | Complete all outstanding sprinkler-system works. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 11 | QIC | Install permanent covers and access panels around the bases of all cabinets, replacing temporary scaffolding boards. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 12 | QIC | Install outstanding fire sprinkler cylinders. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 13 | QIC | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 14 | QIC | Complete any outstanding cable-tray installation. | 07 - Final fix / completion | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 15 | QIC | Clean all cabinets internally and externally. | 09 - Final clean / handover | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 16 | QIC | Patch, make good and repaint the walls after completion of outstanding works. | 06 - Finishes / painting | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 17 | QIC | Install wall panel DDC-02 after prerequisite works are complete. | 02 - Enabling / access / supports | Outstanding |  |  |  | Panel number noted as DDC-02.
2026-10-15 | PB01M10 | A | LV Room | 18 | QIC | Fill and seal wall openings leading into the corridor. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 19 | QIC | Clean the pits below the cabinets and remove debris. | 09 - Final clean / handover | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 20 | QIC | Carry out final room clean and prepare the LV Room for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-15 | PB01M10 | A | LV Room | 21 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M10 | A | LV Room | 22 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M10 | A | LV Room | 23 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 1 | QICDC | Remove the door-frame strap. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 2 | QICDC | Complete final plastering and making good around the door frame and window opening. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 3 | QICDC | Install the window to the window opening. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 4 | QICDC | Complete outstanding works and clearance within the ceiling cavity. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 5 | QICDC | Complete firestopping around the cable-tray penetration within the ceiling cavity. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 6 | QICDC | Complete outstanding cable terminations to electrical boxes within the ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 7 | QICDC | Repair damaged sections of the ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 8 | QICDC | Complete second and third plaster coats to the plasterboard bulkhead. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 9 | QICDC | Remove the temporary light from the ceiling cavity. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 10 | QICDC | Install all outstanding ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 11 | QICDC | Complete painting to the ceiling bulkhead. | 06 - Finishes / painting | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 12 | QICDC | Patch, make good and complete painting to the walls. | 06 - Finishes / painting | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 13 | QICDC | Complete all outstanding MEP third-fix works to the walls. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 14 | QICDC | Complete the epoxy floor finish. | 06 - Finishes / painting | Outstanding
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 15 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 16 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 17 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Receptionist Room Office |  | Receptionist Room Office | 18 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Purchase Office |  | Purchase Office | 1 | QICDC | Remove door-frame strap at floor level. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 2 | QICDC | Install outstanding door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 3 | QICDC | Install windows to window openings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 4 | QICDC | Complete final plastering around the door frame and window openings. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 5 | QICDC | Seal remaining ceiling-cavity penetrations, particularly around cable trays. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 6 | QICDC | Remove protective plastic from AC equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 7 | QICDC | Complete final plastering to the bulkhead around the suspended ceiling. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 8 | QICDC | Repair and make good the ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 9 | QICDC | Install outstanding ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 10 | QICDC | Patch and repair walls ready for final painting. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 11 | QICDC | Complete final wall painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 12 | QICDC | Complete final ceiling and bulkhead painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 13 | QICDC | Complete third-fix electrical installation to walls. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 14 | QICDC | Complete floor finishes. | 06 - Finishes / painting | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 15 | QICDC | Install cover plates to electrical boxes within the ceiling cavity. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 16 | QICDC | Complete final ceiling making good. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Purchase Office |  | Purchase Office | 17 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Purchase Office |  | Purchase Office | 18 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Purchase Office |  | Purchase Office | 19 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Flower Room |  | Flower Room | 1 | QICDC | Grout and secure the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 2 | QICDC | Install door following frame grouting. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 3 | QICDC | Install door hardware and ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 4 | QICDC | Complete plastering around the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 5 | QICDC | Complete wall tiling around the door frame. | 06 - Finishes / painting | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 6 | QICDC | Complete installation of MEP wall boxes. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 7 | QICDC | Complete outstanding wall tiling after MEP clearance. | 06 - Finishes / painting | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 8 | QICDC | Grout completed wall tiles. | 06 - Finishes / painting | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 9 | QICDC | Apply required sealant to wall tiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 10 | QICDC | Complete outstanding floor tiles, including three missing locations. | 06 - Finishes / painting | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 11 | QICDC | Cut MEP pipework flush with finished floor where required. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 12 | QICDC | Complete drain installation at four locations. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 13 | QICDC | Complete MEP sink installation. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 14 | QICDC | Complete MEP third fix following wall tiling and grouting. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 15 | QICDC | Complete insulation to high-level pipework. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 16 | QICDC | Install suspended ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 17 | QICDC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 18 | QICDC | Install outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Flower Room |  | Flower Room | 19 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Flower Room |  | Flower Room | 20 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Flower Room |  | Flower Room | 21 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Flower Room |  | Flower Room | 22 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Holdings Store |  | Holdings Store | 1 | QICDC | Grout and secure the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 2 | QICDC | Remove door-frame bracing after grout completion. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 3 | QICDC | Install the door. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 4 | QICDC | Install door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 5 | QICDC | Complete MEP containment around the door frame and provide clearance. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 6 | QICDC | Replaster chased electrical conduits around the door area. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 7 | QICDC | Complete tiling around the door. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 8 | QICDC | Confirm whether remaining MEP boxes within tiled walls are required. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 9 | QICDC | Complete four outstanding wall tiles. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 10 | QICDC | Install missing strip of wall tiles at the internal corner. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 11 | QICDC | Cut or remove the redundant pipe protruding from the floor. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 12 | QICDC | Provide suitable cover or grate and make good the floor location. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 13 | QICDC | Complete wall-tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 14 | QICDC | Complete floor-tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 15 | QICDC | Complete sealant to wall and floor tiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 16 | QICDC | Confirm all MEP installation above suspended ceiling is complete. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 17 | QICDC | Complete remaining first- and second-fix MEP works, including fire and life-safety provisions. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 18 | QICDC | Install suspended ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 19 | QICDC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 20 | QICDC | Install light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 21 | QICDC | Install electrical cover plates above ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 22 | QICDC | Complete outstanding insulation above ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 23 | QICDC | Cap and seal redundant high-level openings. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Holdings Store |  | Holdings Store | 24 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holdings Store |  | Holdings Store | 25 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holdings Store |  | Holdings Store | 26 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holdings Store |  | Holdings Store | 27 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 1 | QICDC | MEP team to confirm all required provisions are complete and provide clearance for cold-room installation. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 2 | QICDC | Cold-room team to commence cold-room installation immediately after MEP clearance. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 3 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 4 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 5 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 6 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 7 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Holding Cold Room |  | Holding Cold Room | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 1 | QICDC | Urgently grout and secure the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 2 | QICDC | Complete plastering around the door frame following grouting. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 3 | QICDC | Remove temporary door-frame brace. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 4 | QICDC | Commence wall tiling immediately in available cleared areas. | 06 - Finishes / painting | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 5 | QICDC | Fill redundant wall chases. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 6 | QICDC | MEP team to provide floor clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 7 | QICDC | Complete floor waterproofing. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 8 | QICDC | Complete floor screed. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 9 | QICDC | Continue high-level wall tiling while low-level works progress. | 06 - Finishes / painting | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 10 | QICDC | Confirm ceiling and high-level MEP first and second fix and provide clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 11 | QICDC | Pull lighting power cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 12 | QICDC | Complete high-level firestopping and fire sealant. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 13 | QICDC | Complete outstanding high-level plastering. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 14 | QICDC | Complete insulation to high-level MEP services. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 15 | QICDC | Remove protective plastic from AC equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 16 | QICDC | Complete wall-tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 17 | QICDC | Complete floor-tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 18 | QICDC | Complete sealant to wall and floor tiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 19 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 20 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 21 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 22 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Bottle Washroom |  | Bottle Washroom | 23 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 1 | QICDC | Provide and install the missing door frame and door assembly. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 2 | QICDC | Urgently grout and secure the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 3 | QICDC | Complete plastering around the door frame following grouting. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 4 | QICDC | Remove temporary door-frame brace. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 5 | QICDC | Commence wall tiling immediately in available cleared areas. | 06 - Finishes / painting | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 6 | QICDC | Fill redundant wall chases. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 7 | QICDC | MEP team to provide floor clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 8 | QICDC | Complete floor waterproofing. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 9 | QICDC | Complete floor screed. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 10 | QICDC | Continue high-level wall tiling while low-level works progress. | 06 - Finishes / painting | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 11 | QICDC | Confirm ceiling and high-level MEP first and second fix and provide clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 12 | QICDC | Pull lighting power cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 13 | QICDC | Complete high-level firestopping and fire sealant. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 14 | QICDC | Complete outstanding high-level plastering. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 15 | QICDC | Complete insulation to high-level MEP services. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 16 | QICDC | Remove protective plastic from AC equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 17 | QICDC | Complete wall-tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 18 | QICDC | Complete floor-tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 19 | QICDC | Complete sealant to wall and floor tiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 20 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 21 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 22 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 23 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Clean Bottle Hold |  | Clean Bottle Hold | 24 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Training Room |  | Training Room | 1 | QICDC | Install missing single door frame and door. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Training Room |  | Training Room | 2 | QICDC | Grout single door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 3 | QICDC | Remove or cut temporary single-door-frame bracing. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Training Room |  | Training Room | 4 | QICDC | Install single-door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Training Room |  | Training Room | 5 | QICDC | Install missing double-door frame and door assembly. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Training Room |  | Training Room | 6 | QICDC | Grout double-door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 7 | QICDC | Complete plastering around both door openings. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 8 | QICDC | Complete plastering to chased wall areas. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 9 | QICDC | Repair walls damaged or marked during construction. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 10 | QICDC | Repair or grind defective floor slab ready for finishes. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 11 | QICDC | Inspect and rectify visible floor-slab cracks. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Training Room |  | Training Room | 12 | QICDC | Remove excess concrete around the circular column. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Training Room |  | Training Room | 13 | QICDC | MEP team to confirm wall provisions and provide clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Training Room |  | Training Room | 14 | QICDC | Complete MEP third fix to wall-mounted items. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Training Room |  | Training Room | 15 | QICDC | Provide ceiling MEP clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Training Room |  | Training Room | 16 | QICDC | Complete suspended ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Training Room |  | Training Room | 17 | QICDC | Repair damaged ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Training Room |  | Training Room | 18 | QICDC | Complete second and third plaster coats to plasterboard ceiling. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 19 | QICDC | Install permanent lights. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Training Room |  | Training Room | 20 | QICDC | Install electrical cover plates above ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Training Room |  | Training Room | 21 | QICDC | Install AC grilles. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Training Room |  | Training Room | 22 | QICDC | Remove surplus plasterboard stored above ceiling. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Training Room |  | Training Room | 23 | QICDC | Repair ceiling cut-outs or install required access panels. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Training Room |  | Training Room | 24 | QICDC | Install outstanding electrical floor box. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Training Room |  | Training Room | 25 | QICDC | Grout and concrete around floor box. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Training Room |  | Training Room | 26 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Training Room |  | Training Room | 27 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Training Room |  | Training Room | 28 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Training Room |  | Training Room | 29 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Training Room |  | Training Room | 30 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Learning Centre |  | Learning Centre | 1 | QICDC | Complete plaster around both door frames after installation. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 2 | QICDC | Complete remaining plaster snagging. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 3 | QICDC | MEP team to provide wall clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 4 | QICDC | Complete final wall painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 5 | QICDC | Complete MEP third fix to wall-mounted items. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 6 | QICDC | Confirm correct requirements and sizes for seven electrical floor boxes. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 7 | QICDC | Install seven floor boxes. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 8 | QICDC | Complete floor-box terminations. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 9 | QICDC | Grout and concrete around floor boxes. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 10 | QICDC | Provide high-level MEP clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 11 | QICDC | Confirm ductwork is correctly positioned. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 12 | QICDC | Install duct and AC grilles. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 13 | QICDC | Repair damaged ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 14 | QICDC | Complete ceiling-grid installation. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 15 | QICDC | Clean dust from room and walls before ceiling close-up. | 09 - Final clean / handover | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 16 | QICDC | Complete second and third plaster coats to plasterboard ceiling and sand. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 17 | QICDC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 18 | QICDC | Install permanent light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 19 | QICDC | Remove surplus and stored materials. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 20 | QICDC | Complete ceiling-level MEP third fix. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 21 | QICDC | Install final floor covering. | 06 - Finishes / painting | Outstanding
2026-10-15 | Learning Centre |  | Learning Centre | 22 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Learning Centre |  | Learning Centre | 23 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Learning Centre |  | Learning Centre | 24 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | UPS Room |  | UPS Room | 1 | QICDC | Confirm all high-level MEP works and provide clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 2 | QICDC | Complete high-level cable tray. | 03 - MEP first / second fix | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 3 | QICDC | Pull all outstanding cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 4 | QICDC | Complete high-level cable terminations. | 07 - Final fix / terminations | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 5 | QICDC | Install high-level electrical cover plates. | 07 - Final fix / terminations | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 6 | QICDC | Install missing sprinkler heads. | 07 - Final fix / terminations | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 7 | QICDC | Install permanent lights. | 07 - Final fix / terminations | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 8 | QICDC | Complete third-fix wall sockets, power points and accessories. | 07 - Final fix / terminations | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 9 | QICDC | Patch and make good walls. | 04 - Wet works / builder works | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 10 | QICDC | Remove redundant ceiling fixings and patch affected areas. | 04 - Wet works / builder works | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 11 | QICDC | Repaint ceiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 12 | QICDC | Complete fire-suppression system. | 03 - MEP first / second fix | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 13 | QICDC | Seal low-level wall penetration near entrance. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 14 | QICDC | Remove redundant wall fixings behind panels and patch holes. | 04 - Wet works / builder works | Outstanding
2026-10-15 | UPS Room |  | UPS Room | 15 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | UPS Room |  | UPS Room | 16 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | UPS Room |  | UPS Room | 17 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | UPS Room |  | UPS Room | 18 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | CBR Room |  | CBR Room | 1 | QICDC | Confirm high-level MEP completion and provide clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 2 | QICDC | Patch, touch up and repaint ceiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 3 | QICDC | Confirm all cables have been pulled to wall accessories. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 4 | QICDC | Install cover plates to wall-mounted accessories. | 07 - Final fix / terminations | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 5 | QICDC | Complete plaster repairs to walls. | 04 - Wet works / builder works | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 6 | QICDC | Complete wall painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 7 | QICDC | Complete wall-mounted MEP third fix. | 07 - Final fix / terminations | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 8 | QICDC | Install threaded rods and supports for lighting. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 9 | QICDC | Install permanent lights. | 07 - Final fix / terminations | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 10 | QICDC | Install missing sprinkler head. | 07 - Final fix / terminations | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 11 | QICDC | Complete fire-suppression installation. | 03 - MEP first / second fix | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 12 | QICDC | Repair penetrations above the door behind containment. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 13 | QICDC | Complete partially installed high-level conduits or remove if redundant. | 03 - MEP first / second fix | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 14 | QICDC | Complete high-level plaster and paint touch-ups. | 06 - Finishes / painting | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 15 | QICDC | Retain required containment penetrations and seal five redundant wall openings. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 16 | QICDC | Complete final wall painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 17 | QICDC | Touch up epoxy floor and skirting. | 06 - Finishes / painting | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 18 | QICDC | Fill redundant drilled and fixing holes. | 04 - Wet works / builder works | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 19 | QICDC | Remove redundant fixings behind Eaton cabinets and repair holes. | 04 - Wet works / builder works | Outstanding
2026-10-15 | CBR Room |  | CBR Room | 20 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | CBR Room |  | CBR Room | 21 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Main Locker Room |  | Main Locker Room | 1 | QICDC | Complete plastering around the installed single-door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 2 | QICDC | Complete tiling around the single-door opening. | 06 - Finishes / painting | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 3 | QICDC | Fill and plaster the cavity above the double-door head. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 4 | QICDC | Complete tiling around the double-door opening. | 06 - Finishes / painting | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 5 | QICDC | Confirm final ceiling MEP clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 6 | QICDC | Complete remaining ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 7 | QICDC | Repair damaged ceiling-grid sections. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 8 | QICDC | Install remaining ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 9 | QICDC | Cut and install ceiling tiles correctly around sprinkler heads. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 10 | QICDC | Install remaining lights. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 11 | QICDC | Install AC grilles. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 12 | QICDC | Install missing floor tiles near the door threshold. | 06 - Finishes / painting | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 13 | QICDC | Complete installation of outstanding lockers. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 14 | QICDC | Complete sealant to floor expansion joints. | 06 - Finishes / painting | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 15 | QICDC | Install missing floor grates. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 16 | QICDC | Remove or relocate temporary AC unit obstructing works. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 17 | QICDC | Install missing floor tile behind the temporary AC unit. | 06 - Finishes / painting | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 18 | QICDC | Paint the door frame. | 06 - Finishes / painting | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 19 | QICDC | Install outstanding door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Main Locker Room |  | Main Locker Room | 20 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Main Locker Room |  | Main Locker Room | 21 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Main Locker Room |  | Main Locker Room | 22 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Main Locker Room |  | Main Locker Room | 23 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Main Locker Room |  | Main Locker Room | 24 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Female Locker Room |  | Female Locker Room | 1 | QICDC | Complete plastering around the installed single-door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 2 | QICDC | Complete tiling around the single-door opening. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 3 | QICDC | Fill and plaster the cavity above the double-door head. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 4 | QICDC | Complete tiling around the double-door opening. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 5 | QICDC | Confirm final ceiling MEP clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 6 | QICDC | Complete remaining ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 7 | QICDC | Repair damaged ceiling-grid sections. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 8 | QICDC | Install remaining ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 9 | QICDC | Cut and install ceiling tiles correctly around sprinkler heads. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 10 | QICDC | Install remaining lights. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 11 | QICDC | Install AC grilles. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 12 | QICDC | Install missing floor tiles near the door threshold. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 13 | QICDC | Complete installation of outstanding lockers. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 14 | QICDC | Complete sealant to floor expansion joints. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 15 | QICDC | Install missing floor grates. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 16 | QICDC | Remove or relocate temporary AC unit obstructing works. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 17 | QICDC | Install missing floor tile behind the temporary AC unit. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 18 | QICDC | Paint the door frame. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 19 | QICDC | Install outstanding door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Locker Room |  | Female Locker Room | 20 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Locker Room |  | Female Locker Room | 21 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Locker Room |  | Female Locker Room | 22 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Locker Room |  | Female Locker Room | 23 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Locker Room |  | Female Locker Room | 24 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 1 | QICDC | Install floor drains in all shower areas. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 2 | QICDC | Install shower taps, mixers and shower heads. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 3 | QICDC | Complete wall tiling around all door frames internally and externally. | 06 - Finishes / painting | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 4 | QICDC | Provide MEP ceiling clearance throughout WC and shower areas. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 5 | QICDC | Complete ceiling grids. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 6 | QICDC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 7 | QICDC | Install extract and ventilation grilles in shower areas. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 8 | QICDC | Install door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 9 | QICDC | Install sanitary ware. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 10 | QICDC | Complete outstanding WC-area accessories above sanitary ware where required. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 11 | QICDC | Check and adjust sprinkler heads to finished ceiling level. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 12 | QICDC | Install grilles in plasterboard ceilings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 13 | QICDC | Complete wall and floor tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 14 | QICDC | Complete finishing and grouting around tiled door frames. | 06 - Finishes / painting | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 15 | QICDC | Complete ceiling-level MEP grilles and finishes. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 16 | QICDC | Install sinks and basins. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 17 | QICDC | Install bench tops. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 18 | QICDC | Complete remaining wall tiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 19 | QICDC | Complete small tile cuts between floor tiles and thresholds. | 06 - Finishes / painting | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 20 | QICDC | Complete tiling around window openings. | 06 - Finishes / painting | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 21 | QICDC | Complete MEP third fix to tiled wall areas. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 22 | QICDC | Complete remaining ceilings throughout toilets and showers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 23 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 24 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 25 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 26 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Male Toilets and Showers |  | Male Toilets and Showers | 27 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 1 | QICDC | Install floor drains in all shower areas. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 2 | QICDC | Install shower taps, mixers and shower heads. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 3 | QICDC | Complete wall tiling around all door frames internally and externally. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 4 | QICDC | Provide MEP ceiling clearance throughout WC and shower areas. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 5 | QICDC | Complete ceiling grids. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 6 | QICDC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 7 | QICDC | Install extract and ventilation grilles in shower areas. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 8 | QICDC | Install door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 9 | QICDC | Install sanitary ware. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 10 | QICDC | Complete outstanding WC-area accessories above sanitary ware where required. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 11 | QICDC | Check and adjust sprinkler heads to finished ceiling level. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 12 | QICDC | Install grilles in plasterboard ceilings. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 13 | QICDC | Complete wall and floor tile grouting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 14 | QICDC | Complete finishing and grouting around tiled door frames. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 15 | QICDC | Complete ceiling-level MEP grilles and finishes. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 16 | QICDC | Install sinks and basins. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 17 | QICDC | Install bench tops. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 18 | QICDC | Complete remaining wall tiling. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 19 | QICDC | Complete small tile cuts between floor tiles and thresholds. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 20 | QICDC | Complete tiling around window openings. | 06 - Finishes / painting | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 21 | QICDC | Complete MEP third fix to tiled wall areas. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 22 | QICDC | Complete remaining ceilings throughout toilets and showers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 23 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 24 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 25 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 26 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Female Toilets and Showers |  | Female Toilets and Showers | 27 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | Furniture Room |  | Furniture Room | 1 | QICDC | Remove temporary door-frame brace. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 2 | QICDC | Complete plaster repairs around the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 3 | QICDC | Install door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 4 | QICDC | Seal high-level openings and penetrations. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 5 | QICDC | MEP team to provide ceiling clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 6 | QICDC | Install permanent lights. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 7 | QICDC | Remove stored door frames from the room and install at designated locations. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 8 | QICDC | Prepare and rectify floor substrate for final covering. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 9 | QICDC | Remove temporary protection from mechanical equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 10 | QICDC | Complete wall-mounted MEP terminations and final fix. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 11 | QICDC | Complete final wall plaster touch-ups. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 12 | QICDC | Complete final wall painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 13 | QICDC | Complete penetration sealing and required firestopping. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 14 | QICDC | Install electrical cover plates. | 07 - Final fix / terminations | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 15 | QICDC | Cut or remove excessive and redundant threaded rods. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 16 | QICDC | Remove concrete splatter and debris at wall-to-floor junction and make good. | 04 - Wet works / builder works | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 17 | QICDC | Complete high-level MEP pipework. | 03 - MEP first / second fix | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 18 | QICDC | Remove protective plastic from ductwork. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | Furniture Room |  | Furniture Room | 19 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | Furniture Room |  | Furniture Room | 20 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | SECURE STORE | A | SECURE STORE | 1 | QIC | Complete routing, pulling and dressing of all loose high-level cables into approved cable tray, conduit or designated containment; provide permanent supports and maintain separation from mechanical services. | 03 - MEP first / second fix | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 2 | QIC | Identify and label all cables, then complete terminations at wall boxes, devices, panels and final connection points in accordance with approved drawings and schedules. | 07 - Final fix / terminations | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 3 | QIC | Complete and secure all flexible conduits: trim excessive lengths, connect with approved glands/adaptors, maintain the required bend radius and add independent supports. | 03 - MEP first / second fix | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 4 | QIC | Confirm the status of coiled, spare and abandoned cables or conduits; remove redundant materials, or label, cap and secure approved spare capacity in an accessible location. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 5 | QIC | Install the correct devices, accessories and permanent cover plates to all open electrical and ELV boxes after cable terminations are complete. | 07 - Final fix / terminations | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 6 | QIC | Confirm the approved purpose of the rough rectangular wall opening; install the required grille or access panel, or infill with compatible blockwork and finish flush if redundant. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 7 | QIC | Seal all high-level wall and soffit penetrations around pipes, conduits, cables and containment using the approved tested firestop system after concealed services are inspected. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 8 | QIC | Make good all chases, rough openings and damaged plaster around wall boxes, penetrations and the door-frame return; form straight edges and a flush, crack-free substrate. | 04 - Wet works / builder works | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 9 | QIC | After MEP completion and firestopping approval, prepare patched surfaces and apply matching primer and finish coats to walls and soffits. | 06 - Finishes / painting | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 10 | QIC | Complete coordinated final inspection, electrical testing, defect rectification and cleaning; remove offcuts and temporary supports and submit test results and close-out photographs. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-15 | SECURE STORE | A | SECURE STORE | 11 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | SECURE STORE | A | SECURE STORE | 12 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | SECURE STORE | A | SECURE STORE | 13 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | SECURE STORE | A | SECURE STORE | 14 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 1 | QIC | Identify the exposed low-level cable tails, route them through suitable conduit or containment, terminate them in the intended enclosure or device, and make good the wall opening after testing. | 07 - Final fix / terminations | Outstanding
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 2 | QIC | Complete terminations to both recessed wall boxes, fit the specified electrical/ELV devices and aligned cover plates, then patch the surrounding wall finish. | 07 - Final fix / terminations | Outstanding
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 3 | QIC | Secure or terminate the loose service above the doorway, complete the ceiling closure at the door head, and make good the surrounding plaster after MEP clearance. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 4 | QIC | Complete and secure all high-level flexible conduits and cable tails, connect them to the equipment and wall boxes with approved glands, fit covers, and electrically test the completed circuits. | 07 - Final fix / terminations | Outstanding
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 5 | QIC | Refit and permanently secure the loose pipe insulation and vapour-barrier jacket; seal all joints and exposed ends to provide continuous, undamaged insulation. | 03 - MEP first / second fix | Outstanding
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 6 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 9 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | EMER EQUIP | A | EMER EQUIP | 10 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01B19 | A | Security Office | 1 | QIC | Identify all loose and coiled cables at recessed wall boxes, complete the required electrical and ELV terminations, and fit the specified devices with aligned permanent faceplates. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 2 | QIC | Route exposed low-level cable tails at wall-to-floor junctions through suitable conduit or containment, terminate them at the intended points, and close the wall openings after testing. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 3 | QIC | Secure, support and dress all loose high-level cables above doors and openings, then terminate them at the designated equipment or junction boxes with approved glands. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 4 | QIC | Complete all flexible-conduit connections to high-level equipment and electrical boxes; trim excess lengths, maintain bend radii, provide supports and enclose exposed conductors. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 5 | QIC | Complete electrical testing and functional verification of all newly terminated power, lighting and ELV points; rectify defects and label circuits and devices as required. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 6 | QIC | Refit and permanently secure loose or damaged pipe and duct insulation, restore the vapour-barrier jacket, and seal all joints and exposed ends continuously. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 7 | QIC | Complete all remaining high-level MEP services and supports within the open ceiling zone, remove temporary materials, and obtain coordinated inspection before closure. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 8 | QIC | Complete the metal door set, including door leaf, lockset, handles, closer, seals and other specified hardware; adjust for correct alignment, clearance and smooth operation. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 9 | QIC | Grout, plaster and make good around door frames and all service-box openings, forming straight reveals and flush, crack-free edges without contaminating completed fittings. | 04 - Wet works / builder works | Outstanding
2026-10-15 | PB01B19 | A | Security Office | 10 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01B19 | A | Security Office | 11 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01B19 | A | Security Office | 12 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01B19 | A | Security Office | 13 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01B19 | A | Security Office | 14 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PANTRY | A | PANTRY | 1 | QIC | After MEP inspection, close the remaining ceiling and bulkhead openings with the approved system and seal all service penetrations using the specified firestopping where required. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PANTRY | A | PANTRY | 2 | QIC | Complete plaster repairs to wall and window reveals, prepare all patched surfaces, and apply matching primer and final paint for a uniform finish throughout the Security Office. | 06 - Finishes / painting | Outstanding
2026-10-15 | PANTRY | A | PANTRY | 3 | QIC | Remove debris, cable offcuts, markings and temporary protection; clean the room and complete a coordinated final snag inspection before secure handover. | 09 - Final clean / handover | Outstanding
2026-10-15 | PANTRY | A | PANTRY | 4 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PANTRY | A | PANTRY | 5 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PANTRY | A | PANTRY | 6 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PANTRY | A | PANTRY | 7 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LOOBY | A | LOOBY | 1 | QIC | Identify the exposed low-level cable tails, route them through approved conduit or containment, terminate them at the intended device or enclosure, and make good the wall opening after testing. | 03 - MEP first / second fix | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 2 | QIC | Complete the recessed electrical point beside the doorway, then plaster and make good the rough wall and door reveal to form straight, flush and crack-free edges. | 04 - Wet works / builder works | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 3 | QIC | Secure and terminate the coiled cables at the door jamb in suitable electrical boxes, fit the required accessories or cover plates, and make good the surrounding chase and reveal. | 07 - Final fix / terminations | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 4 | QIC | Complete termination at the open wall box, fit the specified device and permanent faceplate, then patch the adjacent rough plaster to match the finished wall plane. | 07 - Final fix / terminations | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 5 | QIC | Complete and inspect all above-ceiling MEP services, cable containment and supports, remove loose temporary cables, then install the remaining ceiling tiles or panels. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 6 | QIC | Route, support and terminate all loose cable coils above and beside the wall opening, then complete plastering and straight-edge making-good around the full opening. | 03 - MEP first / second fix | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 7 | QIC | Complete the cable termination within the recessed wall box, install the correct accessory and cover plate, and repair the surrounding wall chase and plaster finish. | 07 - Final fix / terminations | Outstanding
2026-10-15 | LOOBY | A | LOOBY | 8 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LOOBY | A | LOOBY | 9 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LOOBY | A | LOOBY | 10 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LOOBY | A | LOOBY | 11 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LOOBY | A | LOOBY | 12 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LOOBY | A | LOOBY | 13 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | LOOBY | A | LOOBY | 14 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 1 | QIC | Complete the wiring at the open recessed wall box, install the specified device and permanent faceplate, and patch the surrounding wall finish after electrical testing. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 2 | QIC | Identify, segregate and dress all coiled high-level power and ELV cables into the designated containment, provide permanent supports, label each cable and route it to its final point. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 3 | QIC | Secure and route the loose cable coil within approved containment, complete its termination at the intended device or panel, and remove or cap any redundant cable after confirmation. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 4 | QIC | Complete terminations at all wall-mounted power and ELV boxes, fit the specified outlets, data points and cover plates, label them, and function-test every point. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 5 | QIC | Complete, support and terminate all hanging ceiling cables and flexible conduits, verify coordination with ducts, sprinklers and trays, and remove temporary loose services. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 6 | QIC | Finish and align the suspended-ceiling grid, complete all above-ceiling MEP works and inspections, then install the remaining ceiling tiles or panels without unsupported cut sections. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 7 | QIC | Complete the remaining high-level containment, conduit supports and service connections at the perimeter, then close wall points and ceiling voids only after coordinated inspection and testing. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 8 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 9 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 10 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 11 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 12 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01M11 | A | SECU.CONTROL RM | 13 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 1 | QIC | Complete installation of all remaining door frames and door leaves, including grouting, alignment, seals, ironmongery and adjustment for smooth operation. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 2 | QIC | Install all outstanding electrical sockets, outlets and accessories using the completed wiring; fit cover plates, label circuits and carry out electrical and functional testing. | 07 - Final fix / terminations | Outstanding
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 3 | QIC | Prepare all unfinished and repaired surfaces, complete the remaining paint coats and final touch-ups, and leave a uniform finish free from marks, damage and overspray. | 06 - Finishes / painting | Outstanding
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 4 | QIC | Complete all outstanding ceiling framing, service coordination, closures, tiles or panels and final finishes after above-ceiling MEP inspection and approval. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 5 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 6 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 7 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 8 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | STAFF ENTRANCE LOOBY | A | STAFF ENTRANCE LOOBY | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | IDF | A | IDF | 1 | QIC | Complete connection and termination of all remaining cables; route, dress, label and permanently support hanging cables within the approved containment, then test the completed circuits. | 07 - Final fix / terminations | Outstanding
2026-10-15 | IDF | A | IDF | 2 | QIC | Organize all cables emerging from the floor into suitable conduit, trunking or floor-entry containment; secure and protect them, maintain bend radii and seal the floor entry as required. | 03 - MEP first / second fix | Outstanding
2026-10-15 | IDF | A | IDF | 3 | QIC | Prepare unfinished and repaired surfaces, complete all remaining paint coats and final touch-ups, and leave a uniform finish free from marks, damage and overspray. | 06 - Finishes / painting | Outstanding
2026-10-15 | IDF | A | IDF | 4 | QIC | Install all remaining electrical sockets, outlets, accessories and lighting fixtures; fit cover plates, label circuits and complete electrical and functional testing. | 07 - Final fix / terminations | Outstanding
2026-10-15 | IDF | A | IDF | 5 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | IDF | A | IDF | 6 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | IDF | A | IDF | 7 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | IDF | A | IDF | 8 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | IDF | A | IDF | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 1 | QIC | Complete installation of the Nurse Office door and frame, including grouting, seals, ironmongery, alignment and making good around the opening. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 2 | QIC | Complete all Nurse Office electrical wiring, connections and accessories; route and permanently secure loose ceiling cables in approved containment, then test the circuits. | 07 - Final fix / terminations | Outstanding
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 3 | QIC | Complete the Nurse Office ceiling installations and final finishes, then prepare surfaces and complete all remaining painting and touch-ups. | 06 - Finishes / painting | Outstanding
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 4 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 5 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 6 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 7 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | NURSES OFFICE | A | NURSES OFFICE | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 1 | QIC | Install all remaining Examination Room electrical sockets, outlets and accessories; complete wiring and connections at their designated locations and test all circuits. | 07 - Final fix / terminations | Outstanding
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 2 | QIC | Complete all remaining Examination Room ceiling framing, service coordination, closures, tiles or panels and final finishes after above-ceiling inspection. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 3 | QIC | Complete installation of all Examination Room doors and frames, including grouting, ironmongery, seals, alignment and making good around openings. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 4 | QIC | Complete all outstanding Examination Room finishing works, rectify defective workmanship and leave wall, floor and joinery interfaces neat, uniform and ready for snagging. | 06 - Finishes / painting | Outstanding
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 5 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 6 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | EXAM OFFFICE | A | EXAM OFFFICE | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | TOL | A | TOL | 1 | QIC | Install all missing ceramic wall and floor tiles in the Toilet Area; align joints, complete grouting and sealant, and leave a clean, even and watertight finish. | 04 - Wet works / builder works | Outstanding
2026-10-15 | TOL | A | TOL | 2 | QIC | Complete all Toilet Area electrical wiring, connections and accessories; route, dress and permanently secure loose ceiling cables in approved containment and test the circuits. | 07 - Final fix / terminations | Outstanding
2026-10-15 | TOL | A | TOL | 3 | QIC | Complete all remaining Toilet Area ceiling framing, coordinated service openings, closures, tiles or panels and final finishes after MEP inspection. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | TOL | A | TOL | 4 | QIC | Install the missing Toilet Area door and frame, including grouting, seals, ironmongery, alignment and final making good around the opening. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | TOL | A | TOL | 5 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TOL | A | TOL | 6 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TOL | A | TOL | 7 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TOL | A | TOL | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | TOL | A | TOL | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | INTER RM | A | INTER RM | 1 | QIC | Complete all pending electrical wiring and connections, and safely terminate all exposed cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | INTER RM | A | INTER RM | 2 | QIC | Install all missing electrical sockets and associated accessories. | 07 - Final fix / terminations | Outstanding
2026-10-15 | INTER RM | A | INTER RM | 3 | QIC | Properly route and secure all hanging cables, then complete all unfinished ceiling works. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | INTER RM | A | INTER RM | 4 | QIC | Install the missing door frame, complete related finishing and painting works, then carry out final cleaning and housekeeping. | 09 - Final clean / handover | Outstanding
2026-10-15 | INTER RM | A | INTER RM | 5 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | INTER RM | A | INTER RM | 6 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | INTER RM | A | INTER RM | 7 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | INTER RM | A | INTER RM | 8 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | INTER RM | A | INTER RM | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | TRAI MAN | A | TRAI MAN | 1 | QIC | Complete all pending electrical wiring and connections, and properly route and secure all hanging ceiling cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | TRAI MAN | A | TRAI MAN | 2 | QIC | Install all missing electrical sockets and complete the installation of all lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-15 | TRAI MAN | A | TRAI MAN | 3 | QIC | Complete all unfinished ceiling works, including painting and final finishing. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | TRAI MAN | A | TRAI MAN | 4 | QIC | Install the missing door and complete all related finishing works and outstanding wall painting. | 06 - Finishes / painting | Outstanding
2026-10-15 | TRAI MAN | A | TRAI MAN | 5 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRAI MAN | A | TRAI MAN | 6 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRAI MAN | A | TRAI MAN | 7 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRAI MAN | A | TRAI MAN | 8 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | TRAI MAN | A | TRAI MAN | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | STORE | A | STORE | 1 | QIC | No specific inspection comments were provided; conduct a joint inspection and issue a room-specific snag list. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | STORE | A | STORE | 2 | QIC | Verify the status of all electrical, socket and lighting installations and record any outstanding work. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | STORE | A | STORE | 3 | QIC | Verify the condition and completion status of the ceiling, doors and architectural finishes. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | STORE | A | STORE | 4 | QIC | Verify all MEP and life-safety installations, connections and access requirements. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | STORE | A | STORE | 5 | QIC | Confirm housekeeping, safe access and any close-out requirements for the room. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | STORE | A | STORE | 6 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STORE | A | STORE | 7 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STORE | A | STORE | 8 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STORE | A | STORE | 9 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STORE | A | STORE | 10 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | STORE | A | STORE | 11 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | STORE | A | STORE | 12 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01E05 | A | RECEPTION | 1 | QIC | Install and connect all missing electrical sockets. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01E05 | A | RECEPTION | 2 | QIC | Properly route, secure and conceal all exposed and hanging electrical cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | PB01E05 | A | RECEPTION | 3 | QIC | Install all missing door frames, doors, trims and accessories. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01E05 | A | RECEPTION | 4 | QIC | Complete all unfinished ceiling works, including missing ceiling panels and covers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01E05 | A | RECEPTION | 5 | QIC | Complete all pending painting, making-good and finishing works. | 06 - Finishes / painting | Outstanding
2026-10-15 | PB01E05 | A | RECEPTION | 6 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E05 | A | RECEPTION | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E05 | A | RECEPTION | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E05 | A | RECEPTION | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E05 | A | RECEPTION | 10 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 1 | QIC | Install all missing electrical sockets, complete pending electrical connections, and properly terminate exposed cables. | 07 - Final fix / terminations | Outstanding
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 2 | QIC | Properly route, secure and conceal all hanging cables from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 3 | QIC | Complete all unfinished ceiling works, including missing ceiling panels and covers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 4 | QIC | Install all missing door frames and doors. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 5 | QIC | Complete all door trims, accessories and related finishing works. | 07 - Final fix / completion | Outstanding
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 6 | QIC | Commence and complete all required painting and final touch-up works. | 06 - Finishes / painting | Outstanding
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 7 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 8 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 9 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 10 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 11 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | TRANING ROOM | A | TRANING ROOM | 12 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | MAN OFF | A | MAN OFF | 1 | QIC | No specific inspection comments were provided; conduct a joint inspection and issue a room-specific snag list. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | MAN OFF | A | MAN OFF | 2 | QIC | Verify electrical, ceiling, door and finishing works and record any outstanding items. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | MAN OFF | A | MAN OFF | 3 | QIC | Confirm safety, housekeeping and handover requirements following the joint inspection. | 01 - Verify / inspect / confirm | Outstanding
2026-10-15 | MAN OFF | A | MAN OFF | 4 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | MAN OFF | A | MAN OFF | 5 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | MAN OFF | A | MAN OFF | 6 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | MAN OFF | A | MAN OFF | 7 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | MAN OFF | A | MAN OFF | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | MAN OFF | A | MAN OFF | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | MAN OFF | A | MAN OFF | 10 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | HR OFF | A | HR OFF | 1 | QIC | HR Office: Install and connect missing electrical sockets, complete pending wiring, and secure exposed cables. | 03 - MEP first / second fix | Outstanding
2026-10-15 | HR OFF | A | HR OFF | 2 | QIC | HR Office: Complete unfinished ceiling works, install missing panels, and rectify and secure exposed metal ceiling framework. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | HR OFF |  | HR OFF | 3 | QIC | HR Office: Complete all pending painting, making-good and finishing works. | 06 - Finishes / painting | Outstanding
2026-10-15 | HR OFF |  | HR OFF | 4 | QIC | Attached Bathroom: Complete pending electrical wiring and connections and install all missing sockets. | 07 - Final fix / terminations | Outstanding
2026-10-15 | HR OFF |  | HR OFF | 5 | QIC | Attached Bathroom: Properly terminate, secure and safely enclose all exposed electrical cables. | 07 - Final fix / terminations | Outstanding
2026-10-15 | HR OFF | A | HR OFF | 6 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | HR OFF | A | HR OFF | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | HR OFF | A | HR OFF | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | HR OFF | A | HR OFF | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | HR OFF | A | HR OFF | 10 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 1 | QIC | Install and connect all missing electrical sockets. | 07 - Final fix / terminations | Outstanding
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 2 | QIC | Install all missing doors and frames. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 3 | QIC | Complete all trims, accessories and related door finishing works. | 07 - Final fix / completion | Outstanding
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 4 | QIC | Complete all unfinished ceiling works, including missing ceiling panels and covers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 5 | QIC | Commence and complete all pending painting, making-good and finishing works. | 06 - Finishes / painting | Outstanding
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 6 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | PB01E14 |  | BREAKOUT SPACE | 10 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 1 | QIC | Install and connect all missing electrical sockets and complete outstanding electrical wiring and connections. | 07 - Final fix / terminations | Outstanding
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 2 | QIC | Install all missing doors and complete all related trims, accessories and finishing works. | 02 - Enabling / access / supports | Outstanding
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 3 | QIC | Complete all unfinished ceiling works, including missing panels and covers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 4 | QIC | Commence and complete all pending painting, making-good and finishing works. | 06 - Finishes / painting | Outstanding
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 5 | QIC | Install warning signs and safety barriers around all floor openings, then remove construction debris and complete general housekeeping. | 09 - Final clean / handover | Outstanding
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 6 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-15 | LEARNING CENTRE |  | LEARNING CENTRE | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01E32 | A | Male Ablution Room | 1 | QIC | Door ironmongery is missing; supply and install all required door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 2 | QIC | Complete installation of tiles around the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 3 | QIC | Complete tiling in the ablution room near the opening. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 4 | QIC | Once all tiling is complete, complete all tile grouting. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 5 | QIC | Replace the ablution-room threshold; existing threshold is too short. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 6 | QIC | Ensure all fire sealant within the ceiling cavity is complete. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 7 | QIC | Complete all MEP works in the ceiling cavity, including cable pulling and terminations. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 8 | QIC | Remove the temporary light from the ceiling cavity. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 9 | QIC | Repair or replace the damaged suspended-ceiling frame. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 10 | QIC | Install lights to the ceiling frame. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 11 | QIC | Install ceiling tiles and cut required openings for sprinklers. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 12 | QIC | Complete missing tile grouting and close all gaps in grout joints. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 13 | QIC | Rectify lipping to two wall tiles near the entrance to the prayer room. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 14 | QIC | Complete installation of taps to the wash / ablution area. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 15 | QIC | Complete ceiling-to-floor tiling. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 16 | QIC | Complete ceiling closure / making good around cable-tray openings. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 17 | QIC | Complete remaining mechanical installation works. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 18 | QIC | Remove remaining temporary lights. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 19 | QIC | Ensure ceiling clearance is provided prior to ceiling close-up. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 20 | QIC | Install the ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 21 | QIC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 22 | QIC | Complete sealant to the ablution area. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 23 | QIC | Complete tiling around floor wastes. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01E32 | A | Male Ablution Room | 24 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | PB01E32 | A | Male Ablution Room | 25 | QIC | Complete all wall-mounted electrical and MEP third-fix works, including sockets, switches, outlets, data points, controls, accessories, permanent cover plates and identification labels. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | PB01E32 | A | Male Ablution Room | 26 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | PB01E32 | A | Male Ablution Room | 27 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | PB01E32 | A | Male Ablution Room | 28 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | Prayer Room | A | Prayer Room | 1 | QIC | Grind and clean the floor to prepare it for floor coverings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 2 | QIC | Grind and patch uneven floor areas to achieve a flat substrate ready for carpet, including corners, wall edges and column bases. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 3 | QIC | Patch the hole in the wall near the back wall adjacent to the circular column. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 4 | QIC | Complete plastering around the entrance into the prayer room. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 5 | QIC | Complete all MEP third-fix items to the walls. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 6 | QIC | Complete final painting to all walls. | 06 - Finishes / painting | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 7 | QIC | Install the floor covering / carpet. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 8 | QIC | Ensure all high-level ceiling-cavity penetrations are sealed. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 9 | QIC | Ensure all electrical cables are dropped and ready for installation of lights. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 10 | QIC | Install all light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 11 | QIC | Complete outstanding sections of the suspended-ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 12 | QIC | Rectify suspended-ceiling suspension lines so they are straight and correctly connected to the ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 13 | QIC | Ensure MEP clearance is provided above the ceiling before ceiling close-up. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 14 | QIC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 15 | QIC | Clean the room and remove tile debris and other waste. | 09 - Final clean / handover | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 16 | QIC | Install air-conditioning grilles. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 17 | QIC | Ensure all required cover plates are fitted. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 18 | QIC | Repair the damaged ceiling grid near the circular column. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 19 | QIC | Cut off and remove all threaded rod that is no longer required. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Prayer Room | A | Prayer Room | 20 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Prayer Room | A | Prayer Room | 21 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | Employee Lounge | A | Employee Lounge | 1 | QIC | Supply and install missing door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 2 | QIC | Grind and level the floor at the room entrance. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 3 | QIC | Complete final plaster coat and making good around the door frame, ready for final painting. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 4 | QIC | Apply first and second coats of paint to the walls. | 06 - Finishes / painting | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 5 | QIC | Ensure all cables have been pulled for wall sockets and complete final fix. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 6 | QIC | Repair plaster finish at the base of the walls. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 7 | QIC | Patch and sand the lower sections of all walls. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 8 | QIC | Repair damaged wall corners. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 9 | QIC | Remove miscellaneous stored materials including aluminium, glass, scaffold and doors, or install them in their intended locations. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 10 | QIC | Repair the damaged ceiling grid near the entrance into the main canteen. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 11 | QIC | Clean and patch the floor ready for final floor finishes. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 12 | QIC | Ensure MEP clearance is provided within the ceiling cavity prior to ceiling close-up. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 13 | QIC | Remove temporary plastic protection from mechanical items. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 14 | QIC | Ensure all electrical works and cable drops are in place for installation of lights. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 15 | QIC | Ensure all required fire sealant within ceiling cavities and penetrations is complete. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 16 | QIC | Complete installation of all remaining ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 17 | QIC | Supply and install air-conditioning grilles within the suspended ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 18 | QIC | Review all walls and complete any plaster touch-up required before final painting. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 19 | QIC | Repair the damaged ceiling grid near the rear right-hand side of the room. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 20 | QIC | Grind and repair the floor near the entrance into the canteen. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Lounge | A | Employee Lounge | 21 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Employee Lounge | A | Employee Lounge | 22 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Employee Lounge | A | Employee Lounge | 23 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 1 | QIC | Remove the door-frame bracing strap. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 2 | QIC | Install the door threshold. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 3 | QIC | Complete floor tiling around MEP pipes; cut/adjust protruding pipes as required to enable tiling. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 4 | QIC | Install MEP floor wastes at four locations. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 5 | QIC | Complete floor grouting once thresholds and floor tiling are complete. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 6 | QIC | Complete wall tiling around the door frame and the door opening into the canteen. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 7 | QIC | Complete skirting tiles near the door openings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 8 | QIC | Grout all wall tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 9 | QIC | Complete sealant to all tiled areas. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 10 | QIC | Confirm ceiling-cavity clearance is provided before ceiling close-up. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 11 | QIC | Install the ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 12 | QIC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 13 | QIC | Install ceiling light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 14 | QIC | Complete MEP third-fix items within the ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 15 | QIC | Complete MEP third-fix items on the walls. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 16 | QIC | Install the benchtop for the sinks. | 07 - Final fix / completion | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 17 | QIC | Install sinks. | 07 - Final fix / completion | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 18 | QIC | Install tapware. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 19 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 20 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Canteen Hand Washroom 1 | A | Canteen Hand Washroom 1 | 21 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Employee Canteen | A | Employee Canteen | 1 | QIC | Address floor levelness and patching as soon as possible. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 2 | QIC | Repair and prepare all floor areas ready to receive tiling. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 3 | QIC | Commence and complete floor tiling. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 4 | QIC | Complete grouting to all floor tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 5 | QIC | Complete sealant to all floor tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 6 | QIC | Complete all skirting tiles within the room. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 7 | QIC | Complete all remaining wall tiling within the room. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 8 | QIC | Complete sealant to all wall tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 9 | QIC | Complete grouting to all wall tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 10 | QIC | Install glazing to the external facade. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 11 | QIC | Install external facade doors. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 12 | QIC | Prepare columns ready to receive final wall finishes. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 13 | QIC | Ensure all cables are pulled to all wall boxes. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 14 | QIC | Complete final fix to all wall-mounted MEP items. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 15 | QIC | Ensure all penetrations in the ceiling cavity to adjoining rooms are sealed. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 16 | QIC | Ensure all MEP services are pulled, positioned and hung ready for suspended-ceiling installation. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 17 | QIC | Obtain MEP clearance above the ceiling before ceiling close-up. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 18 | QIC | Remove all temporary protection from ductwork within the ceiling cavity. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 19 | QIC | Remove all surplus or excessively long threaded rod from the ceiling cavity. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 20 | QIC | Install the suspended-ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 21 | QIC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 22 | QIC | Install light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 23 | QIC | Install air-conditioning grilles. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 24 | QIC | Install sprinkler heads at finished ceiling level. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 25 | QIC | Prepare and make good the floor interfaces to adjoining rooms. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 26 | QIC | Complete floor tiling up to the facade glazing line. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 27 | QIC | Confirm and agree the required finish to the rear of the circular column at the facade glazing line, then complete the approved finish. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Employee Canteen | A | Employee Canteen | 28 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Employee Canteen | A | Employee Canteen | 29 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Employee Canteen | A | Employee Canteen | 30 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 1 | QIC | Remove the door-frame bracing strap. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 2 | QIC | Install the door threshold. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 3 | QIC | Complete floor tiling around MEP pipes; cut/adjust protruding pipes as required to enable tiling. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 4 | QIC | Install MEP floor wastes at four locations. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 5 | QIC | Complete floor grouting once thresholds and floor tiling are complete. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 6 | QIC | Complete wall tiling around the door frame and the door opening into the canteen. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 7 | QIC | Complete skirting tiles near the door openings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 8 | QIC | Grout all wall tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 9 | QIC | Complete sealant to all tiled areas. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 10 | QIC | Confirm ceiling-cavity clearance is provided before ceiling close-up. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 11 | QIC | Install the ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 12 | QIC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 13 | QIC | Install ceiling light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 14 | QIC | Complete MEP third-fix items within the ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 15 | QIC | Complete MEP third-fix items on the walls. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 16 | QIC | Install the benchtop for the sinks. | 07 - Final fix / completion | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 17 | QIC | Install sinks. | 07 - Final fix / completion | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 18 | QIC | Install tapware. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 19 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 20 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Canteen Hand Washroom 2 | A | Canteen Hand Washroom 2 | 21 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Kitchen | A | Kitchen | 1 | QIC | Complete plastering and making good around door frames and door openings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 2 | QIC | Complete all tiling around doors and door frames. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 3 | QIC | Grout the installed door frame. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 4 | QIC | Install outstanding doors. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 5 | QIC | Install all required door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 6 | QIC | Rectify the incorrectly installed door / door frame that is out of plumb. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 7 | QIC | Remove the door-frame brace once the frame is secure and ready. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 8 | QIC | MEP team to confirm clearance and status of all wall MEP items so miscellaneous missing tiles can be installed. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 9 | QIC | Complete tiling within openings around containment and MEP interfaces. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 10 | QIC | Complete all MEP third-fix works. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 11 | QIC | Complete fire sealing to all high-level openings and prepare for ceiling clearance. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 12 | QIC | MEP team to provide high-level ceiling clearance. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 13 | QIC | Install the suspended-ceiling grid. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 14 | QIC | Install high-level light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 15 | QIC | Drop sprinkler services to finished ceiling-grid level. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 16 | QIC | Install ceiling tiles. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 17 | QIC | Complete remaining wall grouting. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 18 | QIC | Complete remaining floor grouting. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 19 | QIC | Complete all outstanding ceiling works. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 20 | QIC | Complete installation of all outstanding high-level MEP items. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 21 | QIC | Inspect all ceiling hangers and ensure they are complete, fit for purpose and correctly attached to support ductwork. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 22 | QIC | Install all outstanding smoke detectors. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Kitchen | A | Kitchen | 23 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Kitchen | A | Kitchen | 24 | QIC | Install or apply the approved final floor finish, including required preparation, skirtings, thresholds, joints, service interfaces, protection and rectification of defects. | 06 - Finishes / painting | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Kitchen | A | Kitchen | 25 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | Kitchen | A | Kitchen | 26 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | AHU Room North | A | AHU Room North | 1 | QIC | Remove the door-frame brace once the frame is secure and ready. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 2 | QIC | Install all required door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 3 | QIC | Patch and repair epoxy flooring adjacent to the door frame. | 04 - Wet works / builder works | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 4 | QIC | Complete final epoxy floor touch-ups after all other works are complete. | 06 - Finishes / painting | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 5 | QIC | Remove masking tape from the epoxy skirting. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 6 | QIC | Inspect ductwork support fixings and install missing base-foot fixings where required. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 7 | QIC | Ensure all cables are pulled to wall-mounted conduits and boxes. | 03 - MEP first / second fix | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 8 | QIC | Install all cover plates and complete final fix to wall-mounted boxes. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 9 | QIC | Review all wall-mounted brackets; install required panels or remove brackets that are no longer required. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 10 | QIC | Remove plastic wrapping and temporary protection from MEP equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 11 | QIC | Cut back excess threaded rod from brackets, particularly at head level, to remove the safety hazard. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 12 | QIC | Review valve layout and locations where access ways for maintenance are narrowed, and rectify as required. | 01 - Verify / inspect / confirm | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 13 | QIC | Install grilles to external openings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 14 | QIC | Complete plastering and making good around all external openings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 15 | QIC | Complete wall / ceiling closure around the riser at the rear of the room. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 16 | QIC | Complete pulling and dressing of all high-level cables. | 03 - MEP first / second fix | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 17 | QIC | Install all permanent light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 18 | QIC | Complete sealant around all wall penetrations and openings. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 19 | QIC | Remove redundant ceiling fixings, patch affected areas, and touch up ceiling paint. | 06 - Finishes / painting | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 20 | QIC | Repair or replace damaged insulation around ductwork. | 03 - MEP first / second fix | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 21 | QIC | Clean all equipment. | 09 - Final clean / handover | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 22 | QIC | Remove loose material and construction debris from under, on top of, and between equipment. | 09 - Final clean / handover | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 23 | QIC | Touch up and paint all circular columns. | 06 - Finishes / painting | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 24 | QIC | Remove all scaffolding when works are complete. | 09 - Final clean / handover | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 25 | QIC | Complete plastering and making good around the large opening. | 04 - Wet works / builder works | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 26 | QIC | Complete installation of all remaining grilles. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 27 | QIC | Remove floor brackets that are no longer in use. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 28 | QIC | Remove temporary cable ties and install proper permanent cable ties. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 29 | QIC | Complete installation of all fire-alarm items. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 30 | QIC | Complete outstanding fire-protection works. | 07 - Final fix / terminations | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 31 | QIC | Remove stored/installation material from behind equipment, including materials used as a temporary workers sleeping area. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 32 | QIC | Patch and make good around all floor wastes. | 04 - Wet works / builder works | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 33 | QIC | Remove plastic protection from high-level MEP items. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 34 | QIC | Remove all unused high-level brackets, threaded rods and supports. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | AHU Room North | A | AHU Room North | 35 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following room-by-room consistency review.
2026-10-18 | AHU Room North | A | AHU Room North | 36 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | AHU Room North | A | AHU Room North | 37 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC RM | A | ELEC RM | 1 | QICA2 | Electrical wires running from the ceiling need organizing. | 03 - MEP first / second fix | Outstanding
2026-10-18 | ELEC RM | A | ELEC RM | 2 | QICA2 | Electrical wires coming out of outlets without plugs. | 07 - Final fix / terminations | Outstanding
2026-10-18 | ELEC RM | A | ELEC RM | 3 | QICA2 | Ceiling wires hanging down that need tidying. | 03 - MEP first / second fix | Outstanding
2026-10-18 | ELEC RM | A | ELEC RM | 4 | QICA2 | Paint and finish work required. | 06 - Finishes / painting | Outstanding
2026-10-18 | ELEC RM | A | ELEC RM | 5 | QICA2 | Lighting work needs adjustment. | 07 - Final fix / terminations | Outstanding
2026-10-18 | ELEC RM | A | ELEC RM | 6 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC RM | A | ELEC RM | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC RM | A | ELEC RM | 8 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC RM | A | ELEC RM | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC RM | A | ELEC RM | 10 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC RM | A | ELEC RM | 11 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B53 | A | General Store | 1 | QICA2 | Install the lighting fixtures; lighting cables are present but no lights are installed. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B53 | A | General Store | 2 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B53 | A | General Store | 3 | QICA2 | Complete the floor finish. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B53 | A | General Store | 4 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B53 | A | General Store | 5 | QICA2 | Repair the cracks in the floor. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01B53 | A | General Store | 6 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B53 | A | General Store | 7 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B53 | A | General Store | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B53 | A | General Store | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B54 | A | HK Store | 1 | QICA2 | Complete all remaining final finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B54 | A | HK Store | 2 | QICA2 | Install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B54 | A | HK Store | 3 | QICA2 | Complete the final finishes around the door. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B54 | A | HK Store | 4 | QICA2 | Properly route, support and terminate the electrical wiring hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01B54 | A | HK Store | 5 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B54 | A | HK Store | 6 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B54 | A | HK Store | 7 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B54 | A | HK Store | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 1 | QICA2 | Organize all scattered materials and complete housekeeping, including removal of bags, water bottles and debris from the floor. | 09 - Final clean / handover | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 2 | QICA2 | Install the door frame and door. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 4 | QICA2 | Complete final painting. | 06 - Finishes / painting | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 5 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 6 | QICA2 | Install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 7 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 8 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | SIGN ITEM STORE | A | SIGN ITEM STORE | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B56 | A | Executive HK | 1 | QICA2 | Organize all scattered materials and complete housekeeping, including removal of bags, water bottles and debris from the floor. | 09 - Final clean / handover | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 2 | QICA2 | Install the door frame and door. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 4 | QICA2 | Complete final painting. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 5 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 6 | QICA2 | Install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 7 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B56 | A | Executive HK | 8 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B56 | A | Executive HK | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B55 | A | HK Office | 1 | QICA2 | Organize all scattered materials and complete housekeeping. | 09 - Final clean / handover | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 2 | QICA2 | Install the door frame and door and complete the associated final finishes. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 3 | QICA2 | Complete all ceiling works and final finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 4 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 5 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 6 | QICA2 | Install sufficient lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 7 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 8 | QICA2 | Properly route, support and terminate all electrical wiring and services hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 9 | QICA2 | Properly install and secure the exposed pipes. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 10 | QICA2 | Provide a suitable fire extinguisher close to the equipment area. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B55 | A | HK Office | 11 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B55 | A | HK Office | 12 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | IDF | A | IDF Room | 1 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | IDF | A | IDF Room | 2 | QICA2 | Install the required air-conditioning equipment; the AC openings are in place but the units are missing. | 07 - Final fix / completion | Outstanding
2026-10-18 | IDF | A | IDF Room | 3 | QICA2 | Install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | IDF | A | IDF Room | 4 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | IDF | A | IDF Room | 5 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | IDF | A | IDF Room | 6 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | IDF | A | IDF Room | 7 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | IDF | A | IDF Room | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 1 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 2 | QICA2 | Complete the missing wall ceramic tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 4 | QICA2 | Properly route, support and terminate all electrical wiring hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 5 | QICA2 | Complete the lighting wiring and install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 6 | QICA2 | Install the missing electrical outlets. | 07 - Final fix / terminations | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 7 | QICA2 | Install the missing door and complete the final finishes around the existing door frame. | 07 - Final fix / completion | Outstanding
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 8 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 9 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 10 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | VALET LAUNDRY | A | Valet Laundry | 11 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 1 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 2 | QICA2 | Complete the missing wall ceramic tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 4 | QICA2 | Properly route, support and terminate all electrical wiring hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 5 | QICA2 | Complete the lighting wiring and install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 6 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 7 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | DIRTY LINEN ROOM | A | DIRTY LINEN ROOM | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | SOIL L | A | SOIL L | 1 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | SOIL L | A | SOIL L | 2 | QICA2 | Complete the missing wall ceramic tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | SOIL L | A | SOIL L | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | SOIL L | A | SOIL L | 4 | QICA2 | Properly route, support and terminate all electrical wiring hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | SOIL L | A | SOIL L | 5 | QICA2 | Complete the lighting wiring and install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | SOIL L | A | SOIL L | 6 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | SOIL L | A | SOIL L | 7 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | SOIL L | A | SOIL L | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | SOIL L | A | SOIL L | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 1 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 2 | QICA2 | Complete the missing wall ceramic tiles. | 04 - Wet works / builder works | Outstanding
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 4 | QICA2 | Properly route, support and terminate all electrical wiring hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 5 | QICA2 | Complete the lighting wiring and install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 6 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 7 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CHEMICAL STORE | A | CHEMICAL STORE | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 1 | QICA2 | Complete the electrical installations and terminations. | 03 - MEP first / second fix | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 2 | QICA2 | Install the missing electrical outlets. | 07 - Final fix / terminations | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 3 | QICA2 | Install all room-specific equipment. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 4 | QICA2 | Install the missing boiler units. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 5 | QICA2 | Install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 6 | QICA2 | Complete the ceiling finishes and properly route, support and terminate exposed wires and pipes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 7 | QICA2 | Repair damaged areas and complete the final finishes around the installed door and frame. | 04 - Wet works / builder works | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 8 | QICA2 | Complete the missing wall and floor ceramic tiling. | 04 - Wet works / builder works | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 9 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 10 | QICA2 | Complete the flooring installation to the required finished standard. | 06 - Finishes / painting | Outstanding
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 11 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 12 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | COMP AND BOILER ROOM | A | Comp and Boiler Room | 13 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B58 | A | Linen Store | 1 | QICA2 | Install the door frame and door. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B58 | A | Linen Store | 2 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B58 | A | Linen Store | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01B58 | A | Linen Store | 4 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B58 | A | Linen Store | 5 | QICA2 | Repair the cracks in the floor. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01B58 | A | Linen Store | 6 | QICA2 | Install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B58 | A | Linen Store | 7 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B58 | A | Linen Store | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B58 | A | Linen Store | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 1 | QICA2 | Install the door frame and door. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 2 | QICA2 | Complete the suspended ceiling, including installation of all missing ceiling panels. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 3 | QICA2 | Install the missing electrical outlets; wiring is present. | 07 - Final fix / terminations | Outstanding
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 4 | QICA2 | Properly terminate the hanging ceiling wiring and install the lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 5 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 6 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 7 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 8 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | LAUNDRY MAN | A | Laundry Man Room | 9 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 1 | QICA2 | Install the missing door frame and door. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 2 | QICA2 | Complete and correctly terminate the electrical wiring and install the missing outlets. | 07 - Final fix / terminations | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 3 | QICA2 | Install the five missing elevators serving this area. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 4 | QICA2 | Resolve the cut and disconnected pipes located on the floor and complete the required connections. | 03 - MEP first / second fix | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 5 | QICA2 | Properly route, support and terminate all wiring hanging from the ceiling. | 03 - MEP first / second fix | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 6 | QICA2 | Complete the ceiling and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 7 | QICA2 | Complete the flooring works. | 06 - Finishes / painting | Outstanding
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 8 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 9 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 10 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 11 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEVATOR LOBBY | A | Elevator Lobby | 12 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CIRCU | A | CIRCU | 1 | QICA2 | Install the missing door frames on both sides. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | CIRCU | A | CIRCU | 2 | QICA2 | Install the missing doors. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | CIRCU | A | CIRCU | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | CIRCU | A | CIRCU | 4 | QICA2 | Complete final paintwork and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | CIRCU | A | CIRCU | 5 | QICA2 | Install the required lighting fixtures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | CIRCU | A | CIRCU | 6 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CIRCU | A | CIRCU | 7 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | CIRCU | A | CIRCU | 8 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01P03 | A | Circulation | 1 | QICA2 | Install the missing door and complete final finishes around the existing door frame. | 07 - Final fix / completion | Outstanding
2026-10-18 | PB01P03 | A | Circulation | 2 | QICA2 | Complete the electrical wiring and install all missing outlets at the designated electrical points. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01P03 | A | Circulation | 3 | QICA2 | Complete the ceiling finishes. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01P03 | A | Circulation | 4 | QICA2 | Commence and complete painting and wall finishes. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01P03 | A | Circulation | 5 | QICA2 | Complete the flooring installation. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01P03 | A | Circulation | 6 | QIC | Complete final wall painting to all applicable non-tiled walls, ceilings, bulkheads, reveals and painted surfaces, including preparation, primer, finish coats and final touch-ups. | 06 - Finishes / painting | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01P03 | A | Circulation | 7 | QIC | Install all outstanding permanent light fittings and associated accessories; complete connections, identification and functional testing. | 07 - Final fix / terminations | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01P03 | A | Circulation | 8 | QIC | Inspect all wall, floor and ceiling service penetrations and openings; complete the approved firestopping or permanent sealing system, including identification and close-out records where applicable. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01P03 | A | Circulation | 9 | QIC | Complete final room cleaning and housekeeping, remove debris, surplus materials and temporary protection, and leave the room secure and ready for handover. | 09 - Final clean / handover | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01P03 | A | Circulation | 10 | QIC | BUJV and the relevant subcontractor shall complete all testing, commissioning and internal snagging, including rectification and supporting records, prior to QIC and DHA inspection. | 08 - Testing / commissioning / snagging | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | Plant Room | A | Plant Room | 1 | QIC -AA | Repair and seal all open joints in the HVAC duct insulation and cladding. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 2 | QIC -AA | Complete outstanding mechanical pipework connections and secure and support all exposed services. | 03 - MEP first / second fix | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 3 | QIC -AA | Complete final electrical terminations, secure loose cables and containment, and install covers to all open boxes and enclosures. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 4 | QIC -AA | Seal all outstanding service penetrations, openings and recesses. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 5 | QIC -AA | Make good all rough and damaged wall surfaces around services, electrical boxes and door openings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 6 | QIC -AA | Repair and make good the unfinished floor surfaces and wall-to-floor junctions. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 7 | QIC -AA | Supply and install the missing main entrance door, door frame and associated door hardware | 02 - Enabling / access / supports | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 8 | QIC -AA | Install outstanding door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 9 | QIC -AA | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 10 | QIC -AA | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 11 | QIC -AA | Carry out final cleaning, remove all construction debris and prepare the Plant Room for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-18 | Plant Room | A | Plant Room | 12 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | ELEC. Room | A | ELEC. Room | 1 | QIC -AA | Complete pulling, dressing, securing and final termination of all outstanding electrical cables. | 03 - MEP first / second fix | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 2 | QIC -AA | Complete and close all cable containment, electrical boxes and cabinet or enclosure sections, including installation of all outstanding covers. | 07 - Final fix / terminations | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 3 | QIC -AA | Fill and seal all outstanding wall openings and recesses. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 4 | QIC -AA | Make good all rough, damaged and uneven wall surfaces around electrical equipment and service routes. | 04 - Wet works / builder works | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 5 | QIC -AA | Supply and install the ELEC. Room double-door set, including frames and door hardware. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 6 | QIC -AA | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 7 | QIC -AA | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 8 | QIC -AA | Remove loose materials and construction debris from the room. | 09 - Final clean / handover | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 9 | QIC -AA | Carry out final room clean and prepare the ELEC. Room for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-18 | ELEC. Room | A | ELEC. Room | 10 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 1 | QIC -AA | Complete the suspended ceiling grid and install all outstanding ceiling tiles and panels. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 2 | QIC -AA | Complete final electrical terminations and secure all loose cables above and below the ceiling. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 3 | QIC -AA | Install all outstanding electrical accessories, cover plates and covers to open wall boxes. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 4 | QIC -AA | Close and seal all outstanding service openings and ceiling voids after completion of MEP works. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 5 | QIC -AA | Make good all rough and unfinished wall surfaces and opening edges. | 04 - Wet works / builder works | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 6 | QIC -AA | Complete the final floor finish throughout the office. | 06 - Finishes / painting | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 7 | QIC -AA | Install all outstanding skirting and complete the wall-to-floor junctions. | 06 - Finishes / painting | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 8 | QIC -AA | Supply and install the outstanding door. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 9 | QIC -AA | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 10 | QIC -AA | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-18 | Chief engineer Off. | A | Chief engineer Off. | 11 | QIC -AA | Remove loose materials and construction debris, carry out final cleaning and prepare the office for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 1 | QIC -AA | Supply and install all outstanding SNC electrical panels in the designated vacant bays. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 2 | QIC -AA | Complete pulling, dressing, securing and final termination of all outstanding electrical cables. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 3 | QIC -AA | Complete all outstanding cable containment connections, transitions and supports around the panel locations. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 4 | QIC -AA | Complete and make good all panel bases, plinths and panel-to-floor junctions. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 5 | QIC -AA | Fill and seal all outstanding wall openings and service penetrations. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 6 | QIC -AA | Make good all rough, damaged and marked wall surfaces around the electrical installations. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 7 | QIC -AA | Install outstanding door ironmongery. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 8 | QIC -AA | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 9 | QIC -AA | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 10 | QIC -AA | Remove loose materials and construction debris, carry out final cleaning and prepare the Electrical room for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-18 | PB01M20 | A | Electrical room | 11 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B68 | A | Service Kitchen | 1 | QIC -AA | Demolish the wall constructed contrary to the latest revision of EI 106 and remove all resulting debris. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 2 | QIC -AA | Supply and install the missing main entrance door, door frame and associated door hardware | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 3 | QIC -AA | Complete all outstanding below-floor service and drainage connections and close the open floor excavation. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 4 | QIC -AA | Complete outstanding pipework and ductwork connections and provide all required supports. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 5 | QIC -AA | Complete final electrical terminations and secure all loose cables and conduits. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 6 | QIC -AA | Install all outstanding electrical accessories, cover plates and covers to open boxes. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 7 | QIC -AA | Seal all outstanding service penetrations and openings after completion of MEP works. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 8 | QIC -AA | Make good all rough and unfinished wall surfaces, openings and edges. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 9 | QIC -AA | Reinstate and complete the final floor screed and floor finish throughout the Service Kitchen. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 10 | QIC -AA | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 11 | QIC -AA | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 12 | QIC -AA | Remove loose materials and construction debris, carry out final cleaning and prepare the Service Kitchen for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding
2026-10-18 | PB01B68 | A | Service Kitchen | 13 | QIC | Complete all outstanding ceiling works, including MEP coordination and clearance, framing or grid, closures, access panels, ceiling tiles or panels, service cut-outs and final making good. | 05 - Close-up / firestopping / ceiling | Outstanding |  |  |  | Added following full basement consistency review, including A2 and AA additions.
2026-10-18 | PB01B67 | A | Service Lobby | 1 | QIC -AA | Supply and install SL05 and SL06, including commissioning and final finishing. | 02 - Enabling / access / supports | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 2 | QIC -AA | Complete outstanding overhead pipework and ductwork connections and provide all required supports. | 03 - MEP first / second fix | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 3 | QIC -AA | Complete final electrical terminations and secure all loose cables and conduits. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 4 | QIC -AA | Install all outstanding electrical accessories, cover plates and covers to open wall boxes. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 5 | QIC -AA | Close and seal all outstanding rectangular recesses, service openings and penetrations after completion of MEP works. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 6 | QIC -AA | Make good all rough and unfinished wall surfaces and edges around door and service openings. | 04 - Wet works / builder works | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 7 | QIC -AA | Complete the ceiling and soffit closures after all overhead services are finished. | 05 - Close-up / firestopping / ceiling | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 8 | QIC -AA | Complete the final floor finish and wall-to-floor junctions throughout the Service Lobby. | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 9 | QIC -AA | Install all outstanding light fittings. | 07 - Final fix / terminations | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 10 | QIC -AA | Complete final painting after all outstanding works and making-good activities are finished | 06 - Finishes / painting | Outstanding
2026-10-18 | PB01B67 | A | Service Lobby | 11 | QIC -AA | Remove loose materials and construction debris, carry out final cleaning and prepare the Service Lobby for snagging and secure close-out. | 08 - Testing / commissioning / snagging | Outstanding

## Sequence Legend
Sequence Ref | Stage | Use / completion gate
01 | Verify / inspect / confirm | Resolve dimensions, design intent, status and access constraints before releasing physical work.
02 | Enabling / access / supports | Remove obstructions and temporary items; install primary frames, supports, panels, cabinets and access components.
03 | MEP first / second fix | Complete containment, trays, conduits, ducts, pipework, cable pulling, droppers and earthing rough-in.
04 | Wet works / builder works | Complete grouting, screed, concrete repairs, plaster/render, tiling, epoxy repairs and substrate work.
05 | Close-up / firestopping / ceiling | Seal penetrations, firestop openings and complete ceiling closure only after concealed services are checked.
06 | Finishes / painting | Complete patching, making good and final paint after disruptive and wet works are finished.
07 | Final fix / terminations | Install devices, lights, sockets, switches, covers, hardware, sprinkler heads and complete terminations after painting where practical.
08 | Testing / commissioning / snagging | Function-test, commission, inspect and rectify snags after final fix.
09 | Final clean / handover | Remove debris and protection, clean equipment and room, then secure for handover.

## Room Summary
Room ID | Room Name | Outstanding Items | Updated List Summary | Value
PB01M01 | Entrance Facility Room | 19 | Input tracker items | 1132
PB01M02 | Main Telephone Room | 19 | New consistency actions | 130
PB01M03 | GSM Room | 22 | Updated total items | 1262
Tetra Room | Tetra Room | 20 | Rooms / areas | 78
Back of House Circulation Corridor | Back of House Circulation Corridor | 25 | Review scope | Full basement including A2 and AA
Generator Room | Generator Room | 41
PB01M06 | MV Room | 21
PB01M37 | Transformer Room - 01 | 13
Transformer Room - 02 | Transformer Room - 02 | 26
Review / Refuge Room | Review Room / Refuge Room | 29
PB01M10 | LV Room | 23
Receptionist Room Office | Receptionist Room Office | 18
Purchase Office | Purchase Office | 19
Flower Room | Flower Room | 22
Holdings Store | Holdings Store | 27
Holding Cold Room | Holding Cold Room | 9
Bottle Washroom | Bottle Washroom | 23
Clean Bottle Hold | Clean Bottle Hold | 24
Training Room | Training Room | 30
Learning Centre | Learning Centre | 24
UPS Room | UPS Room | 18
CBR Room | CBR Room | 21
Main Locker Room | Main Locker Room | 24
Female Locker Room | Female Locker Room | 24
Male Toilets and Showers | Male Toilets and Showers | 27
Female Toilets and Showers | Female Toilets and Showers | 27
Furniture Room | Furniture Room | 20
SECURE STORE | SECURE STORE | 14
EMER EQUIP | EMER EQUIP | 10
PB01B19 | Security Office | 14
PANTRY | PANTRY | 7
LOOBY | LOOBY | 14
PB01M11 | SECU.CONTROL RM | 13
STAFF ENTRANCE LOOBY | STAFF ENTRANCE LOOBY | 9
IDF | IDF | 9
NURSES OFFICE | NURSES OFFICE | 8
EXAM OFFFICE | EXAM OFFFICE | 9
TOL | TOL | 9
INTER RM | INTER RM | 9
TRAI MAN | TRAI MAN | 9
STORE | STORE | 12
PB01E05 | RECEPTION | 10
TRANING ROOM | TRANING ROOM | 12
MAN OFF | MAN OFF | 10
HR OFF | HR OFF | 10
PB01E14 | BREAKOUT SPACE | 10
LEARNING CENTRE | LEARNING CENTRE | 9
PB01E32 | Male Ablution Room | 28
Prayer Room | Prayer Room | 21
Employee Lounge | Employee Lounge | 23
Canteen Hand Washroom 1 | Canteen Hand Washroom 1 | 21
Employee Canteen | Employee Canteen | 30
Canteen Hand Washroom 2 | Canteen Hand Washroom 2 | 21
Kitchen | Kitchen | 26
AHU Room North | AHU Room North | 37
ELEC RM | ELEC RM | 11
PB01B53 | General Store | 9
PB01B54 | HK Store | 8
SIGN ITEM STORE | SIGN ITEM STORE | 9
PB01B56 | Executive HK | 9
PB01B55 | HK Office | 12
IDF | IDF Room | 8
VALET LAUNDRY | Valet Laundry | 11
DIRTY LINEN ROOM | DIRTY LINEN ROOM | 9
SOIL L | SOIL L | 9
CHEMICAL STORE | CHEMICAL STORE | 9
COMP AND BOILER ROOM | Comp and Boiler Room | 13
PB01B58 | Linen Store | 9
LAUNDRY MAN | Laundry Man Room | 9
ELEVATOR LOBBY | Elevator Lobby | 12
CIRCU | CIRCU | 8
PB01P03 | Circulation | 10
Plant Room | Plant Room | 12
ELEC. Room | ELEC. Room | 10
Chief engineer Off. | Chief engineer Off. | 11
PB01M20 | Electrical room | 11
PB01B68 | Service Kitchen | 13
PB01B67 | Service Lobby | 11

## Trade Summary
Primary Trade / Workstream | Number of Actions | Rooms Affected | % of Tracker
General / Other | 68 | 37 | 5.4
Supports / Access / Temporary Works | 14 | 9 | 1.1
Doors / Frames / Ironmongery | 181 | 69 | 14.3
Fixtures / Equipment / Joinery | 27 | 17 | 2.1
Electrical / MEP First & Second Fix | 62 | 30 | 4.9
Mechanical / HVAC / Insulation | 42 | 26 | 3.3
Fire & Life Safety | 11 | 9 | 0.9
Builder Works / Plaster / Concrete | 28 | 22 | 2.2
Tiling / Grouting / Sealant | 74 | 23 | 5.9
Firestopping / Penetrations | 32 | 21 | 2.5
Ceilings / Bulkheads | 264 | 78 | 20.9
Floor Finishes / Screed / Epoxy | 25 | 24 | 2
Painting / Decoration | 52 | 42 | 4.1
Electrical / ELV Third Fix | 114 | 67 | 9
Lighting | 48 | 47 | 3.8
Testing / Commissioning / Snagging | 129 | 78 | 10.2
Cleaning / Handover | 91 | 72 | 7.2

## Room Matrix
Room ID | Room Name | Total Actions | Testing / Commissioning / Snagging | Cleaning / Handover | Lighting | Ceilings / Bulkheads | Firestopping / Penetrations | Doors / Frames / Ironmongery | Painting / Decoration | Floor Finishes / Screed / Epoxy | Tiling / Grouting / Sealant | Electrical / ELV Third Fix | Mechanical / HVAC / Insulation | Fire & Life Safety | Electrical / MEP First & Second Fix | Builder Works / Plaster / Concrete | Fixtures / Equipment / Joinery | Supports / Access / Temporary Works | General / Other
PB01M01 | Entrance Facility Room | 19 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 3 | 1 | 0 | 0 | 2
PB01M02 | Main Telephone Room | 19 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 3 | 1 | 0 | 0 | 2
PB01M03 | GSM Room | 22 | 1 | 2 | 1 | 2 | 1 | 4 | 1 | 0 | 0 | 3 | 0 | 0 | 4 | 0 | 1 | 0 | 2
Tetra Room | Tetra Room | 20 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 0 | 1 | 2 | 0 | 0 | 4 | 0 | 0 | 2 | 1
Back of House Circulation Corridor | Back of House Circulation Corridor | 25 | 1 | 1 | 1 | 1 | 4 | 6 | 1 | 1 | 1 | 3 | 0 | 1 | 1 | 1 | 0 | 0 | 2
Generator Room | Generator Room | 41 | 2 | 2 | 1 | 4 | 3 | 5 | 2 | 1 | 0 | 5 | 5 | 2 | 2 | 2 | 0 | 0 | 5
PB01M06 | MV Room | 21 | 1 | 2 | 1 | 2 | 2 | 4 | 0 | 0 | 0 | 5 | 2 | 1 | 0 | 0 | 0 | 0 | 1
PB01M37 | Transformer Room - 01 | 13 | 2 | 1 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 1
Transformer Room - 02 | Transformer Room - 02 | 26 | 2 | 3 | 0 | 3 | 1 | 3 | 1 | 0 | 0 | 5 | 0 | 1 | 4 | 0 | 0 | 0 | 3
Review / Refuge Room | Review Room / Refuge Room | 29 | 1 | 2 | 1 | 2 | 1 | 4 | 2 | 0 | 7 | 2 | 2 | 0 | 3 | 1 | 0 | 1 | 0
PB01M10 | LV Room | 23 | 1 | 2 | 1 | 2 | 1 | 3 | 1 | 0 | 0 | 5 | 0 | 2 | 2 | 0 | 1 | 0 | 2
Receptionist Room Office | Receptionist Room Office | 18 | 2 | 1 | 0 | 9 | 0 | 2 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
Purchase Office | Purchase Office | 19 | 2 | 1 | 0 | 7 | 0 | 3 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Flower Room | Flower Room | 22 | 1 | 1 | 1 | 4 | 0 | 5 | 0 | 0 | 5 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 1
Holdings Store | Holdings Store | 27 | 1 | 1 | 1 | 6 | 0 | 7 | 0 | 0 | 6 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 2
Holding Cold Room | Holding Cold Room | 9 | 2 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0
Bottle Washroom | Bottle Washroom | 23 | 2 | 1 | 0 | 2 | 1 | 3 | 0 | 1 | 5 | 1 | 1 | 0 | 2 | 1 | 1 | 0 | 2
Clean Bottle Hold | Clean Bottle Hold | 24 | 2 | 1 | 0 | 2 | 1 | 4 | 0 | 1 | 5 | 1 | 1 | 0 | 2 | 1 | 1 | 0 | 2
Training Room | Training Room | 30 | 1 | 1 | 1 | 9 | 0 | 8 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 3
Learning Centre | Learning Centre | 24 | 2 | 2 | 1 | 6 | 0 | 1 | 1 | 0 | 1 | 2 | 2 | 0 | 2 | 0 | 0 | 0 | 4
UPS Room | UPS Room | 18 | 1 | 1 | 1 | 3 | 1 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 3 | 1 | 0 | 0 | 2
CBR Room | CBR Room | 21 | 1 | 1 | 1 | 1 | 2 | 0 | 3 | 1 | 0 | 2 | 0 | 1 | 3 | 1 | 1 | 1 | 2
Main Locker Room | Main Locker Room | 24 | 2 | 1 | 1 | 6 | 0 | 7 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1
Female Locker Room | Female Locker Room | 24 | 2 | 1 | 1 | 6 | 0 | 7 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1
Male Toilets and Showers | Male Toilets and Showers | 27 | 2 | 1 | 0 | 9 | 0 | 4 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 3
Female Toilets and Showers | Female Toilets and Showers | 27 | 2 | 1 | 0 | 9 | 0 | 4 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 3
Furniture Room | Furniture Room | 20 | 1 | 2 | 1 | 1 | 2 | 4 | 2 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 1 | 1
SECURE STORE | SECURE STORE | 14 | 2 | 0 | 0 | 2 | 3 | 1 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 0 | 0
EMER EQUIP | EMER EQUIP | 10 | 3 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0
PB01B19 | Security Office | 14 | 4 | 1 | 0 | 2 | 0 | 4 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0
PANTRY | PANTRY | 7 | 3 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LOOBY | LOOBY | 14 | 3 | 1 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PB01M11 | SECU.CONTROL RM | 13 | 4 | 1 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0
STAFF ENTRANCE LOOBY | STAFF ENTRANCE LOOBY | 9 | 3 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IDF | IDF | 9 | 2 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
NURSES OFFICE | NURSES OFFICE | 8 | 2 | 1 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EXAM OFFFICE | EXAM OFFFICE | 9 | 3 | 1 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOL | TOL | 9 | 2 | 2 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INTER RM | INTER RM | 9 | 2 | 1 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRAI MAN | TRAI MAN | 9 | 1 | 1 | 1 | 4 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STORE | STORE | 12 | 3 | 2 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0
PB01E05 | RECEPTION | 10 | 2 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
TRANING ROOM | TRANING ROOM | 12 | 2 | 1 | 0 | 4 | 0 | 3 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAN OFF | MAN OFF | 10 | 3 | 2 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HR OFF | HR OFF | 10 | 2 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PB01E14 | BREAKOUT SPACE | 10 | 2 | 1 | 0 | 2 | 0 | 3 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LEARNING CENTRE | LEARNING CENTRE | 9 | 2 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PB01E32 | Male Ablution Room | 28 | 2 | 1 | 1 | 11 | 0 | 3 | 0 | 0 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1
Prayer Room | Prayer Room | 21 | 1 | 3 | 2 | 6 | 0 | 0 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 1 | 1
Employee Lounge | Employee Lounge | 23 | 2 | 2 | 1 | 6 | 0 | 3 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 4
Canteen Hand Washroom 1 | Canteen Hand Washroom 1 | 21 | 1 | 1 | 1 | 5 | 0 | 5 | 0 | 0 | 3 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0
Employee Canteen | Employee Canteen | 30 | 1 | 1 | 1 | 9 | 0 | 1 | 0 | 0 | 9 | 0 | 1 | 0 | 2 | 1 | 2 | 0 | 2
Canteen Hand Washroom 2 | Canteen Hand Washroom 2 | 21 | 1 | 1 | 1 | 5 | 0 | 5 | 0 | 0 | 3 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0
Kitchen | Kitchen | 26 | 1 | 1 | 1 | 8 | 0 | 8 | 0 | 0 | 4 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0
AHU Room North | AHU Room North | 37 | 1 | 3 | 1 | 3 | 1 | 3 | 2 | 1 | 0 | 1 | 4 | 1 | 5 | 3 | 1 | 5 | 2
ELEC RM | ELEC RM | 11 | 2 | 1 | 0 | 5 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
PB01B53 | General Store | 9 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
PB01B54 | HK Store | 8 | 1 | 1 | 1 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
SIGN ITEM STORE | SIGN ITEM STORE | 9 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PB01B56 | Executive HK | 9 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PB01B55 | HK Office | 12 | 1 | 1 | 1 | 3 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1
IDF | IDF Room | 8 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
VALET LAUNDRY | Valet Laundry | 11 | 1 | 1 | 1 | 4 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DIRTY LINEN ROOM | DIRTY LINEN ROOM | 9 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOIL L | SOIL L | 9 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHEMICAL STORE | CHEMICAL STORE | 9 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COMP AND BOILER ROOM | Comp and Boiler Room | 13 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 1
PB01B58 | Linen Store | 9 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
LAUNDRY MAN | Laundry Man Room | 9 | 1 | 1 | 1 | 2 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ELEVATOR LOBBY | Elevator Lobby | 12 | 2 | 1 | 0 | 4 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2
CIRCU | CIRCU | 8 | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PB01P03 | Circulation | 10 | 2 | 1 | 0 | 3 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plant Room | Plant Room | 12 | 1 | 0 | 1 | 1 | 1 | 3 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 0
ELEC. Room | ELEC. Room | 10 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 1
Chief engineer Off. | Chief engineer Off. | 11 | 1 | 0 | 1 | 3 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1
PB01M20 | Electrical room | 11 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 1
PB01B68 | Service Kitchen | 13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1
PB01B67 | Service Lobby | 11 | 2 | 0 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0